## 1
KALINGA - SLS GOLD
CURRENT RATING
BASIC ASSUMPTIONS FOR CURRENT RATING FOR PVC & XLPE CABLES
The current ratings given in Tables are based on the following assumptions :
I) | Maximum conductor temperature |  |  | - | 70°C(FOR PVC INSULATED CABLES)
900C (FOR XLPE INSULATED CABLES)
ii) | Thermal resistivity of soil |  |  | - | 150°C cm/W
iii) | Thermal resistivity of PVC |  |  | - | 650°C cm/W
| Thermal resistivity of XLPE |  |  | - | 3500C cm/W
iv) | Ground temperature |  |  | - | 30°C
v) | Ambient air temperature |  |  | - | 40°C
vi) | Depth of laying |  |  | - | 75cm
KALINGA CURRENT RATINGS (AC) FOR TWO SINGLE-CORE
650/1100 VOLTS UNARMOURED OR NON-MAGNETIC ARMOURED CABLES
ACCORDING TO IS:1554 (Part-I) 1988
NOMINAL |  | LAID DIRECT IN THE |  | IN DUCTS |  |  | IN AIR
AREA OF |  | GROUND
CONDUCTOR
|  | Copper | Aluminium | Copper |  | Aluminium | Copper | Aluminium
mm2 |  | A | A | A |  | A | A | A
1.5 |  | 25 | 21 | 23 |  | 19 | 24 | 18
2.5 |  | 35 | 28 | 31 |  | 25 | 32 | 25
4 |  | 46 | 36 | 42 |  | 33 | 43 | 32
6 |  | 57 | 44 | 54 |  | 42 | 54 | 41
10 |  | 75 | 59 | 72 |  | 56 | 72 | 56
16 |  | 94 | 75 | 92 |  | 71 | 92 | 72
25 |  | 125 | 97 | 120 |  | 93 | 125 | 99
35 |  | 150 | 120 | 140 |  | 110 | 155 | 120
50 |  | 180 | 145 | 165 |  | 130 | 190 | 150
70 |  | 220 | 170 | 200 |  | 155 | 235 | 185
95 |  | 265 | 205 | 230 |  | 180 | 275 | 215
120 |  | 300 | 230 | 255 |  | 200 | 310 | 240
150 |  | 340 | 265 | 280 |  | 220 | 345 | 270
185 |  | 380 | 300 | 305 |  | 240 | 390 | 305
240 |  | 420 | 335 | 340 |  | 270 | 445 | 350
300 |  | 465 | 370 | 370 |  | 295 | 500 | 395
400 |  | 500 | 410 | 405 |  | 335 | 570 | 455
500 |  | 540 | 435 | 430 |  | 355 | 610 | 490
625 |  | 590 | 485 | 465 |  | 395 | 680 | 560

## 2
KALINGA - SLS GOLD
KALINGA CURRENT RATINGS (dc) FOR 650/1100 VOLTS ARMOURED OR UNARMOURED CABLES
According to IS:1554 (Part-I) - 1988
| Laid Direct in the Ground |  |  |  | In Ducts |  |  |  | In Air
Nominal
Area of | Two Singles |  | One Twin |  | Two Singles |  | One Twin |  | Two Singles |  | One Twin
Conductor
| l |  |  | l | l |  |  | l | l |  |  | l
| Copper | Aluminium | Copper | Aluminium | Copper | Aluminium | Copper | Aluminium | Copper | Aluminium | Copper | Aluminium
mm2 | A | A | A | A | A | A | A | A | A | A | A | A
70 | 225 | 175 | 205 | 160 | 215 | 165 | 180 | 140 | 240 | 190 | 195 | 150
95 | 270 | 210 | 245 | 195 | 250 | 195 | 215 | 170 | 285 | 225 | 230 | 180
120 | 310 | 240 | 285 | 220 | 285 | 225 | 240 | 190 | 335 | 260 | 265 | 210
150 | 350 | 270 | 320 | 250 | 325 | 255 | 275 | 215 | 390 | 300 | 310 | 240
185 | 390 | 305 | 360 | 285 | 370 | 285 | 310 | 245 | 445 | 345 | 360 | 280
240 | 455 | 355 | 425 | 330 | 425 | 330 | 360 | 280 | 520 | 405 | 425 | 335
300 | 510 | 400 | 480 | 370 | 475 | 375 | 410 | 320 | 590 | 470 | 490 | 380
400 | 590 | 460 | 550 | 425 | 560 | 435 | 495 | 385 | 710 | 560 | 580 | 450
500 | 650 | 510 | - | - | 630 | 490 | - | - | 800 | 630 | - | -
625 | 760 | 600 | - | - | 730 | 570 | - | - | 960 | 750 | - | -

## 3
KALINGA - SLS GOLD
KALINGA CURRENT RATINGS (ac) FOR THREE -, FOUR-, AND FIVE CORE
650/1100 VOLTS ARMOURED OR UNARMOURED CABLES
ACCORDING TO IS : 1554 (Part-I) 1988
NOMINAL | LAID DIRECT IN THE GROUND |  | IN DUCTS |  | IN AIR
AREA OF
| Copper | Aluminium | Copper | Aluminium | Copper | Aluminium
mm2 | A | A | A | A | A | A
1.5 | 21 | 16 | 17 | 14 | 17 | 13
2.5 | 27 | 21 | 24 | 18 | 24 | 18
4 | 36 | 28 | 30 | 23 | 30 | 23
6 | 45 | 35 | 38 | 30 | 39 | 30
10 | 60 | 46 | 50 | 39 | 52 | 40
16 | 77 | 60 | 64 | 50 | 66 | 51
25 | 99 | 76 | 81 | 63 | 90 | 70
35 | 120 | 92 | 99 | 77 | 110 | 86
50 | 145 | 110 | 125 | 95 | 135 | 105
70 | 175 | 135 | 150 | 115 | 165 | 130
95 | 210 | 165 | 175 | 140 | 200 | 155
120 | 240 | 185 | 195 | 155 | 230 | 180
150 | 270 | 210 | 225 | 175 | 265 | 205
185 | 300 | 235 | 255 | 200 | 305 | 240
240 | 345 | 275 | 295 | 235 | 355 | 280
300 | 385 | 305 | 335 | 260 | 400 | 315
400 | 425 | 335 | 360 | 290 | 455 | 375

## 4
KALINGA - SLS GOLD
KALINGA CURRENT RATINGS (AC) FOR THREE SINGLE CORE
1100 VOLTS UNARMOURED OR NON-MAGNETIC ARMOURED CABLES
ACCORDING TO IS : 1554 (Part-I) 1988
NOMINAL | LAID DIRECT IN THE GROUND |  | IN DUCTS |  | IN AIR
AREA OF
| Copper | Aluminium | Copper | Aluminium | Copper | Aluminium
mm2 | A | A | A | A | A | A
1.5 | 22 | 17 | 21 | 17 | 20 | 15
2.5 | 30 | 24 | 29 | 24 | 27 | 21
4 | 39 | 31 | 38 | 30 | 35 | 27
6 | 49 | 39 | 48 | 37 | 44 | 35
10 | 65 | 51 | 64 | 51 | 60 | 47
16 | 85 | 66 | 83 | 65 | 82 | 64
25 | 110 | 86 | 110 | 84 | 110 | 84
35 | 130 | 100 | 125 | 100 | 130 | 105
50 | 155 | 120 | 150 | 115 | 165 | 130
70 | 190 | 140 | 175 | 135 | 205 | 155
95 | 220 | 175 | 200 | 155 | 245 | 190
120 | 250 | 195 | 220 | 170 | 280 | 220
150 | 280 | 220 | 245 | 190 | 320 | 250
185 | 305 | 240 | 260 | 210 | 370 | 290
240 | 345 | 270 | 285 | 225 | 425 | 335
300 | 375 | 295 | 310 | 245 | 475 | 380
400 | 400 | 325 | 335 | 275 | 550 | 435
500 | 425 | 345 | 355 | 295 | 590 | 480
625 | 470 | 390 | 375 | 320 | 660 | 550
KALINGA - SLS GOLD
KALINGA CURRENT RATINGS (AC) FOR TWIN CORE
650/1100 VOLTS ARMOURED OR UNARMOURED CABLES
ACCORDING TO IS : 1554 (Part-I) 1988
NOMINAL | LAID DIRECT IN THE GROUND |  | IN DUCTS |  | IN AIR
AREA OF
| Copper | Aluminium | Copper | Aluminium | Copper | Aluminium
mm2 | A | A | A | A | A | A
1.5 | 23 | 18 | 20 | 16 | 20 | 16
2.5 | 32 | 25 | 27 | 21 | 27 | 21
4 | 41 | 32 | 35 | 27 | 35 | 27
6 | 50 | 40 | 44 | 34 | 45 | 35
10 | 70 | 55 | 58 | 45 | 60 | 47
16 | 90 | 70 | 75 | 58 | 78 | 59
25 | 115 | 90 | 97 | 76 | 105 | 78
35 | 140 | 110 | 120 | 92 | 125 | 99
50 | 165 | 135 | 145 | 115 | 155 | 125
70 | 205 | 160 | 180 | 140 | 195 | 150
95 | 240 | 190 | 215 | 170 | 230 | 185
120 | 275 | 210 | 235 | 190 | 265 | 210
150 | 310 | 240 | 270 | 210 | 305 | 240
185 | 350 | 275 | 300 | 240 | 350 | 275
240 | 405 | 320 | 345 | 275 | 410 | 325
300 | 450 | 355 | 385 | 305 | 465 | 365
400 | 490 | 385 | 425 | 345 | 530 | 420