## Sheet1
Page-1 PDF Data for House Wiring
KALINGA - SLS GOLD
KALINGA - SLS GOLD COPPER CONDUCTOR FR -PVC INSULATED UNSHEATHED WIRES & CABLES FOR HOUSE &
INDUSTRIAL WIRING CONFORMING TO IS : 694-1990 (Standard PackingOf-90 Mtrs.)
Nominal Area of Conductor |  | No/Diameter of Wires in Conductor |  | Nominal Thickness of Insulation |  | Overall Diameter |  | Maximum D.C. Resistance at 200C |  | Maximum A.C Resistance at 70oC |  |  | Current Rating
mm2 |  | mm |  | mm |  | mm |  | Ohm/km |  | Ohm/km |  |  | Amps
0.75 |  | 24/0.20 |  | 0.6 |  | 2.5 |  | 26 |  | 31.2 |  |  | 7
1 |  | 14/0.30 |  | 0.7 |  | 2.9 |  | 18.1 |  | 21.7 |  |  | 11
1.5 |  | 22/0.30 |  | 0.7 |  | 3.25 |  | 12.1 |  | 14.5 |  |  | 13
2.5 |  | 36/0.30 |  | 0.8 |  | 3.8 |  | 7.41 |  | 8.9 |  |  | 18
4 |  | 56/0.30 |  | 0.8 |  | 4.3 |  | 4.95 |  | 5.94 |  |  | 26
6 |  | 84/0.30 |  | 0.8 |  | 5.2 |  | 3.3 |  | 3.95 |  |  | 33
10 |  | 140/0.30 or 80/0.40 |  | 1 |  | 6.6 |  | 1.91 |  | 2.3 |  |  | 45
16 |  | 126/0.40 |  | 1 |  | 7.6 |  | 1.21 |  | 1.45 |  |  | 60
25 |  | 196/0.40 |  | 1.2 |  | 9.5 |  | 0.78 |  | 0.93 |  |  | 75
35 |  | 276/0.40 |  | 1.2 |  | 10.8 |  | 0.554 |  | 0.665 |  |  | 95
50 |  | 396/0.40 |  | 1.4 |  | 13 |  | 0.386 |  | 0.46 |  |  | 125
KALINGA - KALINGA - SLS GOLD COPPER CONDUCTOR FR - PVC INSULATED UNSHEATHED FLEXIBLE WIRES & CORDS FOR PANEL
& FLEXIBLE WIRING CONFORMING TO IS: 694-1990 (Standard PackingOf-100 Mtrs.)
Nominal Area of Conductor |  | No/Diameter of Wires in Conductor |  | Nominal Thickness of Insulation |  | Maximum D.C Resistance at 20oC |  |  | Maximum A.C Resistance at 70oC |  | Current Rating |  | Overall Dimensions
[13 empty] | Single Core | Twin Parallel | Twin Twisted
mm2 |  | mm |  | mm |  | Ohm/km |  |  | Ohm/km |  | Amps |  | mm | mm | mm
.50 |  | 16/0.20 |  | 0.6 |  | 39 |  |  | 46.8 |  | 4 |  | 2.25 | 4.50 x 2.25 | 4.5
0.75 |  | 24/0.20 |  | 0.6 |  | 26 |  |  | 31.2 |  | 7 |  | 2.45 | 4.90 x 2.45 | 4.9
1 |  | 32/0.20 |  | 0.6 |  | 19.5 |  |  | 21.7 |  | 11 |  | 2.65 | 5.30 x 2.65 | 5.3
1.5 |  | 48/0.20 or 30/0.25 |  | 0.6 |  | 13.3 |  |  | 14.5 |  | 14 |  | 2.9 | 5.80 x 2.90 | 5.8
2.5 |  | 80/0.20 or 50/0.25 |  | 0.7 |  | 7.98 |  |  | 8.9 |  | 19 |  | 3.55 | 7.50 x 3.55 | 7.2
4 |  | 56/0.30 or 128/0.20 |  | 0.8 |  | 4.95 |  |  | 5.94 |  | 26 |  | 4.3 | 8.60 x 4.30 | 8.6
6 |  | 84/0.30 |  | 0.8 |  | 3.3 |  |  | 3.95 |  | 33 |  | 4.9
10 |  | 140/0.30 or 80/0.40 |  | 1 |  | 1.91 |  |  | 2.3 |  | 45 |  | 6.3
16 |  | 126/0.40 |  | 1 |  | 1.21 |  |  | 1.45 |  | 60 |  | 7.4
25 |  | 196/0.40 |  | 1.2 |  | 0.78 |  |  | 0.93 |  | 75 |  | 9.6
35 |  | 276/0.40 |  | 1.2 |  | 0.554 |  |  | 0.665 |  | 95 |  | 10.9
50 |  | 396/0.40 |  | 1.4 |  | 0.386 |  |  | 0.46 |  | 125 |  | 13
70 |  | 360/0.50 |  | 1.4 |  | 0.272 |  |  | 0.326 |  | 170 |  | 14.5
95 |  | 485/0.50 |  | 1.6 |  | 0.206 |  |  | 0.247 |  | 210 |  | 17
120 |  | 610/0.50 |  | 1.6 |  | 0.161 |  |  | 0.193 |  | 235 |  | 19.5
150 |  | 755/0.50 |  | 1.8 |  | 0.129 |  |  | 0.155 |  | 295 |  | 22.5
185 |  | 925/0.50 |  | 2 |  | 0.106 |  |  | 0.127 |  | 340 |  | 24
240 |  | 1221/0.50 |  | 2.2 |  | 0.0801 |  |  | 0.096 |  | 390 |  | 27
300 |  | 1527/0.50 |  | 2.4 |  | 0.0641 |  |  | 0.077 |  | 455 |  | 32
400 |  | 2030/0.5 |  | 2.6 |  | 0.0486 |  |  | 0.058 |  | 590 |  | 35.6
500 |  | 2540/0.5 |  | 2.8 |  | 0.0384 |  |  | 0.046 |  | 630 |  | 42.5
KALINGA - SLS GOLD COPPER CONDUCTOR FR -PVC INSULATED UNSHEATHED WIRES & CABLES FOR HOUSE &
INDUSTRIAL WIRING CONFORMING TO IS : 694-1990 (Standard PackingOf-100 Mtrs.)
Nom. Area of Cond. | Solid Conductor (Single Strand) |  |  | 3 Strand |  |  | 7/19 Strand |  |  | Maximum D.C. Resistance at 20 oC |  | Maximum A.C. Resistance at 70 oC |  | Current Rating
| No/ Dia of Wire | Thickness of Insulation | Overall Diameter | No/ Dia of Wire | Thickness of Insulation | Overall Diameter | No/ Dia of Wire | Thickness of Insulation | Overall Diameter
mm2 | mm | mm | mm | mm | mm | mm | mm | mm | mm | Ohm/Km |  | Ohm/Km |  | Amps
1 | 1/1.12 | 0.70 | 2.65 | 3/0.67 | 0.70 | 2.85 | 7/0.43 | 0.7 | 2.75 | 18.1 |  | 21.7 |  | 11
1.5 | 1/1.38 | 0.70 | 2.9 | 3/0.81 | 0.70 | 3.15 | 7/0.53 | 0.7 | 3.05 | 12.1 |  | 14.5 |  | 13
2.5 | 1/1.78 | 0.80 | 3.5 | 3/1.05 | 0.80 | 3.85 | 7/0.67 | 0.8 | 3.65 | 7.41 |  | 8.9 |  | 18
4 | 1/2.25 | 0.80 | 3.9 |  |  |  | 7/0.85 | 0.8 | 4.3 | 4.61 |  | 5.53 |  | 24
6 | 1/2.76 | 0.80 | 4.4 |  |  |  | 7/1.05 | 0.8 | 4.8 | 3.08 |  | 3.7 |  | 31
10 | - | - | - |  |  |  | 7/1.35 | 1 | 6.1 | 1.83 |  | 2.2 |  | 42
16 | - | - | - |  |  |  | 7/1.70 | 1 | 7.15 | 1.15 |  | 1.38 |  | 57
25 | - | - | - |  |  |  | 7/2.14 | 1.2 | 8.9 | 0.727 |  | 0.87 |  | 71
35 | - | - | - |  |  |  | 7/2.50 | 1.2 | 10 | 0.524 |  | 0.63 |  | 91
50 | - | - | - |  |  |  | 19/1.78 | 1.4 | 11.85 | 0.387 |  | 0.465 |  | 120
R.K.Electrical Industries (India) | [11 empty] | An ISO-9001-2000 Company

## Sheet2
Page-2 PDF Data for House Wiring
KALINGA - SLS GOLD
KALINGA - SLS GOLD FR - PVC INSULATED SINGLE/ MULTICORE PVC SHEATHED CABLES
CONFORMING TO IS: 694-1990 (Standard Packing Of -100 Mtrs.)
Cond Area | Thickness of Insulation (Nominal) | Core Dia | Nominal Thickness of Outer Sheath |  |  |  | Overall Dimensions
|  |  | Single Core | Two Core | Three Core | Four Core | Single Core |  | Two Core Round | Two Core Flat | Three Core Round | Three Core Flat | Four Core Round
mm2 | mm | mm | mm | mm | mm | mm | mm |  | mm | mm | mm | mm | mm
1 | 0.6 | 2.45 | 0.8 | 0.9 | 0.9 | 0.9 | 4.1 |  | 6.8 | 6.80 x 4.35 | 7.2 | 9.20 x 4.35 | 7.8
1.5 | 0.6 | 2.75 | 0.8 | 0.9 | 0.9 | 0.9 | 4.4 |  | 7.4 | 7.40 x 4.65 | 7.8 | 10.1 x 4.65 | 8.5
1.5 | 0.6 | 2.95 | 0.8 | 0.9 | 0.9 | 0.9 | 4.6 |  | 7.8 | 7.80 x 4.85 | 8.25 | 10.70 x 4.85 | 9
2.5 | 0.7 | 3.3 | 0.8 | 1 | 1 | 1 | 4.95 |  | 8.7 | 8.70 x 5.40 | 9.2 | 11.95 x 5.40 | 10.1
2.5 | 0.7 | 3.55 | 0.8 | 1 | 1 | 1 | 5.2 |  | 9.2 | 9.20 x 5.65 | 9.75 | 12.70 x 5.65 | 10.7
4 | 0.8 | 4 | 0.9 | 1 | 1.1 | 1.1 | 5.85 |  | 10.1 | 10.10 x 6.10 | 10.9 | 14.25 x 6.10 | 11.95
4 | 0.8 | 4.3 | 0.9 | 1 | 1.1 | 1.1 | 6.15 |  | 10.7 | 10.70 x 6.40 | 11.55 | 15.15 x 6.40 | 12.7
6 | 0.8 | 4.5 | 0.9 | 1.1 | 1.1 | 1.2 | 6.35 |  | 11.3 | 1130 x 6.80 | 12 | 15.75 x 6.80 | 13.35
6 | 0.8 | 4.9 | 0.9 | 1.1 | 1.1 | 1.2 | 6.75 |  | 12.1 | 12.10 x 7.2 | 12.9 | 16.95 x 7.20 | 14.35
10 | 1 | 5.7 | 0.9 | 1.2 | 1.2 | 1.3 | 7.55 |  | 13.9 | 13.90 x 8.2 | 14.8 | 19.55 x 8.2 | 16.5
10 | 1 | 6.2 | 0.9 | 1.2 | 1.2 | 1.3 | 8.05 |  | 14.9 | 14.90 x 8.70 | 15.9 | 21.05 x 8.70 | 17.7
16 | 1 | 7.3 | 1 | 1.3 | 1.3 | 1.4 | 9.3 |  | 17.2 | 17.20 x 10.00 | 18.35 | 24.40 x 10.00 | 20.4
25 | 1.2 | 9 | 1.1 | 1.4 | 1.5 | 1.6 | 11.2 |  | 20.8 | 20.80 x 11.90 | 22.4 | 29.90 x 12.10 | 25
35 | 1.2 | 10.1 | 1.1 | 1.5 | 1.6 | 1.7 | 12.3 |  | 23.2 | 23.30 x 13.20 | 25 | 33.40 x 13.35 | 27.8
50 | 1.4 | 11.9 | 1.2 | 1.6 | 1.7 | 1.8 | 14.3 |  | 27 | 27.00 x 15.20 | 29.1 | 39.00 x 15.35 | 32.35
KALINGA - SLS GOLD FR-PVC INSULATED SINGLE/ MULTICORE PVC SHEATHED CABLES
CONFORMING TO IS: 694-1990 (Standard Packing Of-100 Mtrs.)
Cond Area | Thickness of Insulation | Core Dia | Nominal Thickness of Outer Sheath |  |  |  |  | Overall Dimensions
|  |  | SingleCore | Two Core | Three Core | Four Core | Five Core | Single Core | Two Core Round | Two Core Flat | Three Core Round | Three Core Flat | Four Core | Five Core
mm2 | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm | mm
0.5 | 0.6 | 2.25 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 4.1 | 6.4 | 6.40 x 4.10 | 6.75 | 8.60 x 4.10 | 7.3 | 7.9
0.75 | 0.6 | 2.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 4.3 | 6.8 | 6.80 x 4.30 | 7.2 | 9.20 x 4.30 | 7.8 | 8.5
1 | 0.6 | 2.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 4.5 | 7.2 | 7.20 x 4.50 | 7.6 | 9.80 x 4.50 | 8.3 | 9.2
1.5 | 0.6 | 2.95 | 0.9 | 0.9 | 0.9 | 1 | 1 | 4.8 | 7.8 | 7.80 x 4.80 | 8.253 | 10.70 x 4.80 | 9.2 | 10
2.5 | 0.7 | 3.65 | 1 | 1 | 1 | 1 | 1 | 5.7 | 9.4 | 9.40 x 5.70 | 10 | 13.00 x 5.70 | 10.9 | 11.9
4 | 0.8 | 4.35 | 1 | 1 | 1 | 1.1 | 1.1 | 6.4 | 10.8 | 10.80 x 6.40 | 11.5 | 15.50 x 6.40 | 12.6 | 14
R.K.Electrical Industries (India) | [10 empty] | An ISO-9001-2000 Company