## Sheet1
QUALITY PLAN
| System : | L.T. Power & Control Cables |  |  | Specification No.IS:1554(Part-I)
PVC insulated and PVC sheathed Armoured type cables as per IS:1554 (Pt.I) 1988.
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8
Raw Materials:
(I) Copper | Finish |  | Visual | 100% | Plant standard | Plant standard | Internal
(ii) Aluminium | Diameter |  | Physical | 100% | Plant standard | Plant standard | - Record | -
| Annealing |  | Physical | Sample | IS:8130-84 | IS:8130 | Internal
Record
| Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | do | -
| Wrapping test |  | Physical | Sample | IS:8130-84 | IS:8130-84 | do
PVC Insulation | Specific Gravity |  | Physical | Sample | Plant Standard | Plant Standard | do | -
| Thermal stability |  | Physical | Sample | IS:5831-84 | IS:5831-84 | do | -
| Tensile/ |  | do | Sample | IS:5831-84 | IS:5831-84 | do | -
Elongation
PVC Inner Sheath | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
Armour Strip | Finish |  | Visual | 100% | IS:3975-90 | IS:3975-90 | do | ISI mark-
| Diameter/ |  | Physical | 100% | IS:3975-90 | IS:3975-90 | do | ed wire
& strip
are being
used.
Mfg. Test
Certificate
available.
PVC Outer Sheath | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
| Thermal stability |  | Physical | Sample | IS:5831-1984 | IS:5831-84 | do
| Tensile/ |  | do | Sample | IS:5831-1984 | IS:5831-84 | do
| Elongation |  | Physical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | do
Contd.. 2..
..2..
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
In Process :
Conductor | Finish |  | Visual | On Line | Plant standard | Plant standard | Internal Rec. | -
| Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
| Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | Internal Rec.
Core | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
| Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C.
Insulation
| Thermal/stability |  | Physical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
Tensile/Elonga-
| tion |  | do | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
| Vol.Resistivity |  | Electrical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
| Spark Testing |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I |  | -
Laying - Up | Circularity |  | Physical | On Line | Plant standard | Plant standard |  | -
| Laid-up-dia |  | Physical | On Line | Design Sheet | Design Sheet |  | -
| High Voltage |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I |  | -
Inner Sheath | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
| Dia-over Inner |  | Physical | On Line | Plant standard | Plant standard |  | -
Sheath
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C. | -
Inner Sheath
Armouring | Uniformity |  | Visual | On Line | Plant standard | Plant standard |  | -
| No. of strip |  | Visual | On Line | Design Sheet | Design Sheet |  | -
| Dia. Over Armour |  | Physical | On Line | Design Sheet | Design Sheet |  | -
| High Voltage |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C. | -
Contd..3..
..3..
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
Outer Sheath | Finish |  | Visual | On Line | Plant standard | Plant standard
| Overall Diameter |  | Physical | On Line | Desogn Sheet | Design Sheet
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R.T.C. | -
Sheath
Finished Product | Embossing |  | Visual | On Line | Design Sheet | Design Sheet | I/R.T.C. | -
Sequential
| Marking |  | Visual | On Line | Plant standard | Plant standard | I/R.T.C. | -
| Routine Test |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | I/R.T.C. | -
| Type Test |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | T.C. | -
|  |  | Electrical | Per Size and Type |  | IS:5831-84 |  | -
[6 empty] | IS:8130-84 |  | -
For K.N.G Wires & Cables
For K.N.G Wires & Cables
Partner. |  |  |  |  | Testing Engineer.

## Sheet2
QUALITY PLAN
| System : | L.T. Power & Control Cables |  |  | Specification No.IS:1554(Part-I)
PVC insulated and PVC sheathed Armoured type cables as per IS:1554 (Pt.I) 1988.
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9
Raw Materials:
Copper | Finish |  | Visual | 100% | Plant standard | Plant standard | Internal
| Diameter |  | Physical | 100% | Plant standard | Plant standard | - Record | -
| Annealing |  | Physical | Sample | IS:8130-84 | IS:8130 | Internal
Record
| Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | do | -
PVC Insulation | Specific Gravity |  | Physical | Sample | Plant Standard | Plant Standard | do | -
| Thermal stability |  | Physical | Sample | IS:5831-84 | IS:5831-84 | do | -
| Tensile/ |  | do | Sample | IS:5831-84 | IS:5831-84 | do | -
Elongation
PVC Inner Sheath | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
PVC Outer Sheath | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
| Thermal stability |  | Physical | Sample | IS:5831-1984 | IS:5831-84 | do
| Tensile/ |  | do | Sample | IS:5831-1984 | IS:5831-84 | do
Elongation
Armour Strip | Finish |  | Visual | 100% | Plant Standard | Plant standard | do | ISI mark-
ed wire
& strip
are being
used.
Mfg. Test
Certificate
| Diameter/ |  | Physical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | do | available.
Contd.. 2..
..2..
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
In Process :
Conductor | Finish |  | Visual | On Line | Plant standard | Plant standard | Internal Rec. | -
| Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
| Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | Internal Rec.
Core | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
| Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C.
Insulation
| Thermal/stability |  | Physical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
Tensile/Elonga-
| tion |  | do | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
| Vol.Resistivity |  | Electrical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
| Spark Testing |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I |  | -
Laying - Up | Circularity |  | Physical | On Line | Plant standard | Plant standard |  | -
| Laid-up-dia |  | Physical | On Line | Design Sheet | Design Sheet |  | -
| High Voltage |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I |  | -
Inner Sheath | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
| Dia-over Inner |  | Physical | On Line | Plant standard | Plant standard |  | -
Sheath
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C. | -
Inner Sheath
Armouring | Uniformity |  | Visual | On Line | Plant standard | Plant standard |  | -
| No. of strip |  | Visual | On Line | Design Sheet | Design Sheet |  | -
| Dia. Over Armour |  | Physical | On Line | Design Sheet | Design Sheet |  | -
| D.C. Resistance |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C. | -
| High Voltage |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | I/R./T.C. | -
Contd..3..
..3..
Component/Operation | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
| Checked |  | of check | check | Document | Norm | Record
Outer Sheath | Finish |  | Visual | On Line | Plant standard | Plant standard
| Overall Diameter |  | Physical | On Line | Desogn Sheet | Design Sheet
| Thickness of |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | I/R.T.C. | -
Sheath
Finished Product | Embossing |  | Visual | On Line | Design Sheet | Design Sheet | I/R.T.C. | -
Sequential
| Marking |  | Visual | On Line | Plant standard | Plant standard | I/R.T.C. | -
| Routine Test |  | Electrical | 100% | IS:1554/Pt.I | IS:1554/Pt.I | I/R.T.C. | -
| Type Test |  | Physical | Sample | IS:1554/Pt.I | IS:1554/Pt.I | T.C. | -
|  |  | Electrical | Per Size and Type |  | IS:5831-84 |  | -
[6 empty] | IS:8130-84 |  | -
For K.N.G Wires & Cables
For K.N.G Wires & Cables
Partner. |  |  |  |  | Testing Engineer.

## Sheet3
QUALITY PLAN
|  | System : | L.T. Power Cables |  |  | Specification No.IS:7098(Part-I)88.
XLPE insulated and PVC sheathed Armoured type cables as per IS:7098 (Pt.I) 1988.
Component/Operation |  | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
|  | Checked |  | of check | check | Document | Norm | Record
1 |  | 2 |  | 3 | 4 | 5 | 6 | 7 | 8
Raw Materials:
(I) Copper |  | Finish |  | Visual | 100% | Plant standard | Plant standard | Internal
(ii) Aluminium |  | Diameter |  | Physical | 100% | Plant standard | Plant standard | - Record | -
|  | Annealing |  | Physical | Sample | IS:8130-84 | IS:8130 | Internal
|  | Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | do | -
|  | Wrapping test |  | Physical | Sample | IS:8130-84 | IS:8130-84 | do | -
XLPE Insulation | Curring |  |  | Electrical | 100% | IS:7098/88 | IS:7098/88 | do | -
|  | Tensile/ |  | do | Sample | IS:5831-84 | IS:5831-84 | do | -
Elongation
PVC Inner Sheath |  | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
|  | Thermal stability |  | Physical | Sample | Plant Standard | Plant standard | do
Armour Strip |  | Finish |  | Visual | 100% | IS:3975-90 | IS:3975-90 | do | ISI mark-
|  | Diameter/ |  | Physical | 100% | IS:3975-90 | IS:3975-90 | do | ed wire
& strip
are being
used.
Mfg. Test
Certificate
available.
PVC Outer Sheath |  | Specific Gravity |  | Physical | Sample | Plant Standard | Plant standard | do
|  | Thermal stability |  | Physical | Sample | IS:5831-1984 | IS:5831-84 | do
|  | Tensile/ |  | do | Sample | IS:5831-1984 | IS:5831-84 | do
|  | Elongation |  | Physical | 100% | IS:7098/Pt.I | IS:7098/Pt.I | do
Contd.. 2..
..2..
Component/Operation |  | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
|  | Checked |  | of check | check | Document | Norm | Record
In Process :
Conductor |  | Finish |  | Visual | On Line | Plant standard | Plant standard | Internal Rec. | -
|  | Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
|  | Resistance |  | Electrical | Sample | IS:8130-84 | IS:8130-84 | Internal Rec.
Core |  | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
|  | Dimensions |  | Physical | On Line | Plant standard | Plant standard |  | -
|  | Thickness of |  | Physical | Sample | IS:7098/Pt.I | IS:7098/Pt.I | I/R./T.C.
Insulation
|  | Thermal/stability |  | Physical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
Tensile/Elonga-
|  | tion |  | do | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
|  | Vol.Resistivity |  | Electrical | Sample | IS:5831-84 | IS:5831-84 | I/R./T.C. | -
|  | Spark Testing |  | Electrical | 100% | IS:7098/Pt.I | IS:7098/Pt.I |  | -
Curring |  | Temperature |  | Electrical | 100% | IS:7098/Pt.I | IS:7098/Pt.I
Laying - Up |  | Circularity |  | Physical | On Line | Plant standard | Plant standard |  | -
|  | Laid-up-dia |  | Physical | On Line | Design Sheet | Design Sheet |  | -
|  | High Voltage |  | Electrical | 100% | IS:7098/Pt.I | IS:7098/Pt.I |  | -
Inner Sheath |  | Finish |  | Visual | On Line | Plant standard | Plant standard |  | -
|  | Dia-over Inner |  | Physical | On Line | Plant standard | Plant standard |  | -
Sheath
|  | Thickness of |  | Physical | Sample | IS:7098/Pt.I | IS:7098/Pt.I | I/R./T.C. | -
Inner Sheath
Armouring |  | Uniformity |  | Visual | On Line | Plant standard | Plant standard |  | -
|  | No. of strip |  | Visual | On Line | Design Sheet | Design Sheet |  | -
|  | Dia. Over Armour |  | Physical | On Line | Design Sheet | Design Sheet |  | -
|  | High Voltage |  | Electrical | 100% | IS:7098/Pt.I | IS:7098/Pt.I | I/R./T.C. | -
Contd..3..
..3..
Component/Operation |  | Characteristic |  | Type/Method | Extent of | Reference | Acceptance | Format of | Remark
|  | Checked |  | of check | check | Document | Norm | Record
Outer Sheath |  | Finish |  | Visual | On Line | Plant standard | Plant standard
|  | Overall Diameter |  | Physical | On Line | Desogn Sheet | Design Sheet
|  | Thickness of |  | Physical | Sample | IS:7098/Pt.I | IS:7098/Pt.I | I/R.T.C. | -
Sheath
Finished Product |  | Embossing |  | Visual | On Line | Design Sheet | Design Sheet | I/R.T.C. | -
Sequential
|  | Marking |  | Visual | On Line | Plant standard | Plant standard | I/R.T.C. | -
|  | Routine Test |  | Electrical | 100% | IS:7098/Pt.I | IS:7098/Pt.I | I/R.T.C. | -
|  | Type Test |  | Physical | Sample | IS:7098/Pt.I | IS:7098/Pt.I | T.C. | -
|  |  |  | Electrical | Per Size |  | IS:5831-84 |  | -
[5 empty] | and type |  | IS:8130-84 |  | -
For K.N.G Wires & Cables
For K.N.G Wires & Cables
Partner. | [5 empty] | Testing Engineer.