## 5
Page -5 PDF Data for Control Cables
KALINGA SLS GOLD 1.5Sq.mm Multi Core Control Cables
KALINGA - SLS GOLD 1.1 KV GRADE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
COPPER CONDUCTOR TO IS 7098 (PART-1) - 1988
No.of Cores X Area | Cond.Min No. of Wires | Nom Thickness of XLPE | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of Cable (approx) |  | Max. D.C Resistance at 200C | Max. A.C Resistance at 900C | Current Rating |  | Short Circuit Rating For 1 Sec.
|  |  |  | Wire Strip | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  | In Ground | In Air
mm2 | No. | mm. | mm. | mm. | mm. | mm. | mm. | mm. | Kg/km | Kg/km | Ohm/km | Ohm/km | Amps | Amps | KA(ms)
2x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 13.5 | 11.5 | 400 | 160 | 12.1 | 15.48 | 23 | 20 | 0.173
3x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 14 | 11.5 | 450 | 185 | 12.1 | 15.48 | 21 | 17 | 0.173
4x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 14.5 | 12.5 | 500 | 215 | 12.1 | 15.48 | 21 | 17 | 0.173
5x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 15.5 | 13 | 540 | 250 | 12.1 | 15.48 | 21 | 17 | 0.173
6x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 16.5 | 14 | 600 | 280 | 12.1 | 15.48 | 15 | 13 | 0.173
7x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 16.5 | 14 | 620 | 300 | 12.1 | 15.48 | 14 | 13 | 0.173
10x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 19.5 | 17 | 800 | 390 | 12.1 | 15.48 | 13 | 11 | 0.173
12x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 20 | 17.5 | 850 | 438 | 12.1 | 15.48 | 12 | 10 | 0.173
14x1.5 | 1 | 0.7 | 0.3 | 1.4 | 1.4 | 2 | 20.5 | 18.5 | 900 | 480 | 12.1 | 15.48 | 11 | 10 | 0.173
16x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 20.5 | 19 | 890 | 540 | 12.1 | 15.48 | 11 | 9 | 0.173
19x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 21.5 | 20 | 960 | 620 | 12.1 | 15.48 | 10 | 9 | 0.173
24x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 24.5 | 23.5 | 1150 | 770 | 12.1 | 15.48 | 9 | 8 | 0.173
27x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 25 | 24 | 1230 | 810 | 12.1 | 15.48 | 9 | 8 | 0.173
30x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 25.5 | 24.5 | 1325 | 890 | 12.1 | 15.48 | 9 | 7 | 0.173
37x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 27.5 | 26 | 1550 | 1050 | 12.1 | 15.48 | 8 | 7 | 0.173
44x1.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.56 | 2 | 30.5 | 29 | 1750 | 1250 | 12.1 | 15.48 | 7 | 6 | 0.173
52x1.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2 | 32 | 30.5 | 2000 | 1400 | 12.1 | 15.48 | 7 | 6 | 0.173
61x1.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2.2 | 34 | 32.5 | 2200 | 1650 | 12.1 | 15.48 | 6 | 6 | 0.173
0.7
KALINGA SLS GOLD 2.5Sq.mm Multi Core Control Cables
KALINGA - SLS GOLD 1.1 KV GRADE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
COPPER CONDUCTOR TO IS 7098 (PART-1) - 1988
No.of Cores X Area | Cond.Min No. of Wires | Nom Thickness of XLPE | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of Cable (approx) |  | Max. D.C Resistance at 200C | Max. A.C Resistance at 900C | Current Rating |  | Short Circuit Rating For 1 Sec.
|  |  |  | Wire Strip | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  | In Ground | In Air
mm2 | No. | mm. | mm. | mm. | mm. | mm. | mm. | mm. | Kg/km | Kg/km | Ohm/km | Ohm/km | Amps | Amps | KA(ms)
2x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 14.5 | 12 | 470 | 190 | 7.41 | 9.48 | 32 | 27 | 0.288
3x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 15 | 12.5 | 520 | 230 | 7.41 | 9.48 | 27 | 24 | 0.288
4x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 15.5 | 13.5 | 580 | 279 | 7.41 | 9.48 | 27 | 24 | 0.288
5x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 16.5 | 14.5 | 660 | 310 | 7.41 | 9.48 | 27 | 24 | 0.288
6x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 17.5 | 15.5 | 720 | 350 | 7.41 | 9.48 | 21 | 18 | 0.288
7x2.5 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 17.5 | 15.5 | 750 | 390 | 7.41 | 9.48 | 20 | 17 | 0.288
10x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 1.8 | 20 | 18.5 | 830 | 510 | 7.41 | 9.48 | 18 | 15 | 0.288
12x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 20.5 | 19 | 920 | 580 | 7.41 | 9.48 | 17 | 14 | 0.288
14x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 21.5 | 20 | 1010 | 650 | 7.41 | 9.48 | 16 | 13 | 0.288
16x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 22.5 | 21.5 | 1110 | 740 | 7.41 | 9.48 | 15 | 12 | 0.288
19x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 23.5 | 22.5 | 1230 | 850 | 7.41 | 9.48 | 14 | 12 | 0.288
24x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 27 | 25.5 | 1490 | 1030 | 7.41 | 9.48 | 13 | 11 | 0.288
27x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.4 | 2 | 27.5 | 26.5 | 1590 | 1130 | 7.41 | 9.48 | 12 | 10 | 0.288
30x2.5 | 1 | 0.7 | 0.3 | 4x0.8 | 1.56 | 2 | 28 | 27 | 1710 | 1230 | 7.41 | 9.48 | 12 | 10 | 0.288
37x2.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2.2 | 30 | 29 | 1990 | 1470 | 7.41 | 9.48 | 11 | 9 | 0.288
44x2.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2.2 | 34 | 33 | 2340 | 1750 | 7.41 | 9.48 | 10 | 9 | 0.288
52x2.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2.2 | 35.5 | 34.5 | 2620 | 2010 | 7.41 | 9.48 | 10 | 8 | 0.288
61x2.5 | 1 | 0.7 | 0.4 | 4x0.8 | 1.56 | 2.2 | 37.5 | 36.5 | 2960 | 2310 | 7.41 | 9.48 | 9 | 8 | 0.288

## 4
Page-4 PDF data for XLPE
(Four Core Cable)
KALINGA - SLS GOLD 1.1 KV GRADE 4 CORE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
ALUMINIUM CONDUCTOR TO IS 7098 (PART-1) 1988
Nom Area of Cond. | Cond. No. of Wires |  | Nom Thick -ness of XLPE Insulation | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of Cable (approx) |  | Max. D.C. Resistance at 200C |  | MaxA.C. Resistance at 900C(Approx) |  | Current Rating |  |  |  | Short Circuit Rating for 1Sec.
[5 empty] | Wire Strip | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  |  |  | In Ground |  | In Air
mm2 | No |  | mm | mm | mm | mm | mm | mm | mm | Kg/km | Kg/km | Ohm/km |  | Ohm/km |  | Amps |  | Amps |  | KA(ms)
| Al | Cu | [7 empty] | Al | Al | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu
4 | 1 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 17 | 15 | 535 | 220 | 7.41 | 4.61 | 9.45 | 5.89 | 34 | 44 | 31 | 40 | 0.38 | 0.57
6 | 1 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 18 | 16.5 | 580 | 255 | 4.61 | 3.08 | 5.89 | 3.93 | 43 | 55 | 40 | 51 | 0.57 | 0.86
10 | 7 | 7 | 0.7 | 0.3 | 1.4 | 1.4 | 1.8 | 20 | 17.5 | 710 | 340 | 3.08 | 1.83 | 3.93 | 2.34 | 57 | 73 | 53 | 70 | 0.94 | 1.4
16 | 7 | 7 | 0.7 | 0.3 | 4x0.8 | 1.4 | 1.8 | 21.5 | 19 | 725 | 425 | 1.91 | 1.15 | 2.43 | 1.472 | 73 | 97 | 70 | 90 | 1.5 | 2.3
25 | 7 | 7 | 0.9 | 0.3 | 4x0.8 | 1.4 | 2 | 24.2 | 22.5 | 925 | 540 | 1.2 | 0.727 | 1.535 | 0.93 | 94 | 122 | 96 | 123 | 2.4 | 3.6
35 | 7 | 7 | 0.9 | 0.3 | 4x0.8 | 1.4 | 2 | 26.5 | 25 | 1100 | 670 | 0.868 | 0.524 | 1.1 | 0.67 | 113 | 146 | 117 | 151 | 3.3 | 5
50 | 7 | 7 | 1 | 0.3 | 4x0.8 | 1.56 | 2 | 30 | 28.5 | 1350 | 860 | 0.641 | 0.387 | 0.82 | 0.495 | 133 | 172 | 142 | 183 | 4.7 | 7.1
70 | 19 | 19 | 1.1 | 0.4 | 4x0.8 | 1.56 | 2.2 | 33 | 32 | 1740 | 1180 | 0.443 | 0.268 | 0.567 | 0.343 | 164 | 211 | 189 | 231 | 6.6 | 10
95 | 19 | 19 | 1.1 | 0.4 | 4x0.8 | 1.56 | 2.2 | 37.2 | 36 | 2140 | 1480 | 0.32 | 0.193 | 0.41 | 0.247 | 196 | 253 | 221 | 285 | 9 | 13.6
120 | 19 | 19 | 1.2 | 0.5 | 4x0.8 | 1.72 | 2.4 | 41 | 39.2 | 2580 | 1825 | 0.253 | 0.153 | 0.324 | 0.197 | 223 | 287 | 257 | 330 | 11.3 | 17.1
150 | 19 | 19 | 1.4 | 0.5 | 4x0.8 | 1.88 | 2.6 | 44.8 | 43.8 | 3060 | 2250 | 0.206 | 0.124 | 0.264 | 0.161 | 249 | 321 | 292 | 375 | 14.2 | 21.4
185 | 37 | 37 | 1.6 | 0.5 | 4x0.8 | 2.04 | 2.8 | 49.6 | 48.8 | 3700 | 2800 | 0.164 | 0.0991 | 0.21 | 0.129 | 282 | 361 | 337 | 430 | 17.5 | 26.4
240 | 37 | 37 | 1.7 | 0.6 | 4x0.8 | 2.2 | 3 | 55.5 | 54.5 | 4650 | 3550 | 0.125 | 0.0754 | 0.16 | 0.1 | 326 | 416 | 399 | 508 | 22.6 | 34.3
300 | 37 | 37 | 1.8 | 0.7 | 4x0.8 | 2.36 | 3.2 | 62.3 | 60.5 | 5600 | 4500 | 0.1 | 0.0601 | 0.13 | 0.081 | 367 | 464 | 456 | 575 | 28.3 | 42.9
400 | 61 | 61 | 2 | 0.7 | 4x0.8 | 2.68 | 3.6 | 70 | 68.5 | 6960 | 5600 | 0.0778 | 0.047 | 0.102 | 0.066 | 418 | 521 | 530 | 661 | 37.7 | 57.1
500 | 61 | 61 | 2.2 | 0.7 | 4x0.8 | 2.84 | 3.8 | 77 | 76 | 8400 | 6850 | 0.0605 | 0.0366 | 0.0809 | 0.053 | 470 | 582 | 612 | 753 | 47.2 | 71.4
630 | 61 | 61 | 2.4 | 0.7 | 4x0.8 | 3 | 4 | 85.5 | 84.5 | 10500 | 8800 | 0.0469 | 0.0283 | 0.064 | 0.043 | 529 | 944 | 707 | 851 | 59.4 | 90

## 3
Page-3 PDF data for XLPE
(Three Core Cables)
KALINGA - SLS GOLD 1.1 KV GRADE THREE CORE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
ALUMINIUM/COPPER CONDUCTOR TO IS 7098 (PART-1) -1988
Nom Area of Cond. | Cond. No. of Wires |  | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of cable (approx) |  | Max. D.C. Resistance at 200C |  | Max. A.C. Resistance at900C |  | Current Rating |  |  |  | Short Circuit Rating for 1 Sec.
|  |  |  | Wire Strip | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  |  |  | In Ground |  | In Air
mm2 | No |  | mm | mm | mm | mm | mm | mm | Kg/Km | Kg/Km | Ohm/km |  | Ohm/km |  | Amps |  | Amps |  | KA(ms)
| Al | Cu | [6 empty] | Al | Al | Al | Cul | Al | Cul | Al | Cul | Al | Cul | Al | Cul
4 | 1 | 1 | 0.3 | 1.4 | 1.24 | 1.8 | 16 | 14 | 500 | 205 | 7.41 | 4.61 | 9.45 | 5.89 | 34 | 44 | 31 | 40 | 0.38 | 0.57
6 | 1 | 1 | 0.3 | 1.4 | 1.24 | 1.8 | 17 | 15 | 570 | 230 | 4.61 | 3.08 | 5.89 | 3.93 | 43 | 55 | 40 | 51 | 0.57 | 0.86
10 | 1 | 7 | 0.3 | 1.4 | 1.24 | 1.8 | 19 | 17 | 660 | 310 | 3.08 | 1.83 | 3.93 | 2.34 | 57 | 73 | 53 | 70 | 0.94 | 1.4
16 | 7 | 7 | 0.3 | 4x0.8 | 1.24 | 1.8 | 21 | 18 | 590 | 365 | 1.91 | 1.15 | 2.43 | 1.472 | 73 | 97 | 70 | 90 | 1.5 | 2.3
25 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 21.8 | 20 | 760 | 400 | 1.2 | 0.727 | 1.535 | 0.93 | 94 | 122 | 96 | 123 | 2.4 | 3.6
35 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 23 | 21.8 | 920 | 520 | 0.868 | 0.524 | 1.1 | 0.67 | 113 | 146 | 117 | 151 | 3.3 | 5
50 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 26 | 24.8 | 1100 | 650 | 0.641 | 0.387 | 0.82 | 0.495 | 133 | 172 | 142 | 183 | 4.7 | 7.1
70 | 19 | 19 | 0.4 | 4x0.8 | 1.56 | 2.2 | 29.5 | 28.5 | 1380 | 890 | 0.443 | 0.268 | 0.567 | 0.343 | 164 | 211 | 179 | 231 | 6.6 | 10
95 | 19 | 19 | 0.4 | 4x0.8 | 1.56 | 2.2 | 32.6 | 31.8 | 1700 | 1160 | 0.32 | 0.193 | 0.41 | 0.247 | 196 | 253 | 221 | 285 | 9 | 13.6
120 | 19 | 19 | 0.4 | 4x0.8 | 1.56 | 2.2 | 36 | 34.8 | 2010 | 1380 | 0.253 | 0.153 | 0.324 | 0.197 | 223 | 287 | 257 | 330 | 11.3 | 17.1
150 | 19 | 19 | 0.5 | 4x0.8 | 1.72 | 2.4 | 41 | 39 | 2410 | 1710 | 0.206 | 0.124 | 0.264 | 0.161 | 249 | 321 | 292 | 375 | 14.2 | 21.4
185 | 37 | 37 | 0.5 | 4x0.8 | 1.88 | 2.6 | 44.8 | 43 | 2920 | 2110 | 0.164 | 0.0991 | 0.21 | 0.129 | 282 | 361 | 337 | 430 | 17.5 | 26.4
240 | 37 | 37 | 0.6 | 4x0.8 | 2.04 | 2.8 | 50.5 | 48.5 | 3630 | 2730 | 0.125 | 0.0754 | 0.16 | 0.1 | 326 | 416 | 399 | 508 | 22.6 | 34.3
300 | 37 | 37 | 0.6 | 4x0.8 | 2.2 | 3 | 55 | 53 | 4350 | 3350 | 0.1 | 0.0601 | 0.13 | 0.081 | 367 | 464 | 456 | 575 | 28.3 | 42.9
400 | 61 | 61 | 0.7 | 4x0.8 | 2.52 | 3.2 | 61 | 60 | 5450 | 4200 | 0.0778 | 0.047 | 0.102 | 0.066 | 418 | 521 | 530 | 661 | 37.7 | 57.1
500 | 61 | 61 | 0.7 | 4x0.8 | 2.68 | 3.6 | 68 | 67 | 6580 | 5250 | 0.0605 | 0.0366 | 0.0809 | 0.053 | 470 | 582 | 612 | 753 | 47.2 | 71.4
630 | 61 | 61 | 0.7 | 4x0.8 | 2.84 | 3.8 | 75.5 | 75 | 8200 | 6650 | 0.0469 | 0.0283 | 0.064 | 0.043 | 529 | 944 | 707 | 851 | 59.4 | 90
(Three & Half Core Cables)
KALINGA - SLS GOLD 1.1 KV GRADE THREE & HALF CORE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
ALUMINIUM / COPPER CONDUCTOR TO IS 7098 (PART-1)-1988
Nom Area of Cond. | Cond. No. of Wires |  | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of cable (approx) |  | Max. D.C. Resistance at 200C |  | Max.A.C. Resistance at 900C (Approx) |  | Current Rating |  |  |  | Short Circuit Rating for 1 Sec.
[5 empty] | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  |  |  | In Ground |  | In Air
mm2 | No |  | mm | mm | mm | mm | mm | mm | Kg/Km | Kg/Km | Ohm/km |  | Ohm/km |  | Amps |  | Amps |  | KA(ms)
| Al | Cu | [6 empty] | Al | Al | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu
3.5x25 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 23 | 22 | 875 | 550 | 1.2 | 0.727 | 1.535 | 0.93 | 94 | 122 | 96 | 123 | 2.4 | 3.6
3.5x35 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 25 | 23.5 | 1020 | 670 | 0.868 | 0.524 | 1.1 | 0.67 | 113 | 146 | 117 | 151 | 3.3 | 5
3.5x50 | 7 | 7 | 0.3 | 4x0.8 | 1.4 | 2 | 28 | 26.5 | 1325 | 875 | 0.641 | 0.387 | 0.82 | 0.495 | 133 | 172 | 142 | 183 | 4.7 | 7.1
3.5x70 | 19 | 19 | 0.4 | 4x0.8 | 1.56 | 2.2 | 32 | 31 | 1600 | 1010 | 0.443 | 0.268 | 0.567 | 0.343 | 164 | 211 | 179 | 231 | 6.6 | 10
3.5x95 | 19 | 19 | 0.4 | 4x0.8 | 1.56 | 2.2 | 36 | 35 | 2000 | 1300 | 0.32 | 0.193 | 0.41 | 0.247 | 196 | 253 | 221 | 285 | 9 | 13.6
3.5x120 | 19 | 19 | 0.4 | 4x0.8 | 1.72 | 2.2 | 40 | 39 | 2350 | 1700 | 0.253 | 0.153 | 0.324 | 0.197 | 223 | 287 | 257 | 330 | 11.3 | 17.1
3.5x150 | 19 | 19 | 0.5 | 4x0.8 | 1.72 | 2.4 | 44 | 42.5 | 2790 | 2050 | 0.206 | 0.124 | 0.264 | 0.161 | 249 | 321 | 292 | 375 | 14.2 | 21.4
3.5x185 | 37 | 37 | 0.5 | 4x0.8 | 1.88 | 2.6 | 49 | 47.5 | 3330 | 2500 | 0.164 | 0.0991 | 0.21 | 0.129 | 282 | 361 | 337 | 430 | 17.5 | 26.4
3.5x240 | 37 | 37 | 0.6 | 4x0.8 | 2.04 | 2.8 | 54 | 53 | 4150 | 3150 | 0.125 | 0.0754 | 0.16 | 0.1 | 326 | 416 | 399 | 508 | 22.6 | 34.3
3.5x300 | 37 | 37 | 0.6 | 4x0.8 | 2.2 | 3 | 59 | 58 | 4950 | 3900 | 0.1 | 0.0601 | 0.13 | 0.081 | 367 | 464 | 456 | 575 | 28.3 | 42.9
3.5x400 | 61 | 61 | 0.7 | 4x0.8 | 2.52 | 3.4 | 67 | 65.5 | 6200 | 4900 | 0.0778 | 0.047 | 0.102 | 0.066 | 418 | 521 | 530 | 661 | 37.7 | 57.1
3.5x500 | 61 | 61 | 0.7 | 4x0.8 | 2.68 | 3.6 | 75 | 73.5 | 7600 | 6100 | 0.0605 | 0.0366 | 0.0809 | 0.053 | 470 | 582 | 612 | 753 | 47.7 | 71.4
3.5x630 | 61 | 61 | 0.7 | 4x0.8 | 3 | 4 | 85 | 84 | 9400 | 7850 | 0.0469 | 0.0283 | 0.064 | 0.043 | 529 | 944 | 707 | 851 | 59.4 | 90

## 2
Page-2 PDF data for XLPE
(Two Core Cables)
KALINGA - SLS GOLD 1.1 KV GRADE TWO CORE XLPE INSULATED ARMOURED AND UNARMOURED CABLE WITH
ALUMINIUM/COPPER CONDUCTOR TO IS 7098 (PART-1) - 1988
Nom Area of Cond. | Cond. No. of Wires |  | Nom. Thickness of XLPE Insulation | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of cable (approx) |  | Max. D.C. Resistance at 200C |  | Max. A.C. Resistance at 900C |  | Current Rating |  |  |  | Short Circuit Rating for 1 Sec.
[5 empty] | Wire Strip | Arm | Unarm | Arm | Unarm | Armoured | Unarmoured |  |  |  |  | In Ground |  | In Air
mm2 | No |  | mm | mm | mm | mm | mm | mm | mm | Kg/Km | Kg/Km | Ohm/km |  | Ohm/km |  | Amps |  | Amps |  | KA(ms)
Al/Cu | Al | Cu | [7 empty] | Al | Al | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu
4 | 1 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 15 | 13 | 460 | 185 | 7.41 | 4.61 | 9.45 | 5.89 | 43 | 56 | 39 | 51 | 0.38 | 0.57
6 | 1 | 1 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 16 | 14 | 525 | 220 | 4.61 | 3.08 | 5.89 | 3.93 | 55 | 71 | 50 | 64 | 0.57 | 0.86
10 | 1 | 7 | 0.7 | 0.3 | 1.4 | 1.24 | 1.8 | 17 | 14.5 | 625 | 270 | 3.08 | 1.83 | 3.93 | 2.34 | 74 | 92 | 67 | 88 | 0.94 | 1.4
16 | 7 | 7 | 0.7 | 0.3 | 1.4 | 1.4 | 1.8 | 17.5 | 15 | 635 | 285 | 1.91 | 1.15 | 2.43 | 1.472 | 91 | 116 | 88 | 113 | 1.5 | 2.3
25 | 7 | 7 | 0.9 | 0.3 | 4x0.8 | 1.4 | 2 | 18.3 | 18 | 665 | 335 | 1.2 | 0.727 | 1.535 | 0.93 | 120 | 152 | 117 | 153 | 2.4 | 3.6
35 | 7 | 7 | 0.9 | 0.3 | 4x0.8 | 1.4 | 2 | 20.5 | 20 | 740 | 400 | 0.868 | 0.524 | 1.1 | 0.67 | 143 | 180 | 145 | 186 | 3.3 | 5
50 | 7 | 7 | 1 | 0.3 | 4x0.8 | 1.4 | 2 | 22.6 | 21.6 | 860 | 515 | 0.641 | 0.387 | 0.82 | 0.495 | 167 | 218 | 176 | 226 | 4.7 | 7.1
70 | 19 | 19 | 1.1 | 0.3 | 4x0.8 | 1.4 | 2 | 25.8 | 25.5 | 1080 | 660 | 0.443 | 0.268 | 0.567 | 0.343 | 204 | 264 | 221 | 284 | 6.6 | 10
95 | 19 | 19 | 1.1 | 0.4 | 4x0.8 | 1.56 | 2.2 | 29.6 | 28.5 | 1350 | 850 | 0.32 | 0.193 | 0.41 | 0.247 | 245 | 314 | 271 | 348 | 9 | 13.6
120 | 19 | 19 | 1.2 | 0.4 | 4x0.8 | 1.56 | 2.2 | 32.65 | 31.5 | 1510 | 1010 | 0.253 | 0.153 | 0.324 | 0.197 | 278 | 357 | 316 | 402 | 11.3 | 17.1
150 | 19 | 19 | 1.4 | 0.4 | 4x0.8 | 1.72 | 2.2 | 35.5 | 34.5 | 1800 | 1210 | 0.206 | 0.124 | 0.264 | 0.161 | 315 | 403 | 362 | 461 | 14.2 | 21.4
185 | 37 | 37 | 1.6 | 0.5 | 4x0.8 | 1.72 | 2.4 | 39.5 | 38.5 | 2100 | 1510 | 0.164 | 0.0991 | 0.21 | 0.129 | 356 | 453 | 420 | 533 | 17.5 | 26.4
240 | 37 | 37 | 1.7 | 0.5 | 4x0.8 | 1.88 | 2.6 | 43 | 42 | 2500 | 1925 | 0.125 | 0.0754 | 0.16 | 0.1 | 407 | 518 | 497 | 633 | 22.6 | 34.3
300 | 37 | 37 | 1.8 | 0.6 | 4x0.8 | 2.04 | 2.8 | 49.5 | 47.5 | 3130 | 2360 | 0.1 | 0.0601 | 0.13 | 0.081 | 463 | 583 | 578 | 732 | 28.3 | 42.9
400 | 61 | 61 | 2 | 0.6 | 4x0.8 | 2.36 | 3 | 55.5 | 54 | 4000 | 3000 | 0.0778 | 0.047 | 0.102 | 0.066 | 528 | 658 | 678 | 841 | 37.7 | 57.1
500 | 61 | 61 | 2.2 | 0.7 | 4x0.8 | 2.52 | 3.4 | 62.5 | 61 | 4900 | 3700 | 0.0605 | 0.0366 | 0.0809 | 0.053 | 592 | 730 | 786 | 967 | 47.2 | 71.4
630 | 61 | 61 | 2.4 | 0.7 | 4x0.8 | 2.68 | 3.6 | 69.5 | 68 | 6050 | 4600 | 0.0469 | 0.0283 | 0.064 | 0.043 | 676 | 814 | 917 | 1103 | 59.4 | 90

## XLPE 1
Page-1 PDF data for XLPE
(Single Core Cables)
KALINGA - SLS GOLD 1.1 KV GRADE SINGLE CORE XLPE INSULATED UNARMOURED AND ARMOURED CABLE WITH
ALUMINIUM /COPPER CONDUCTOR TO IS 7098 (PART-1)-1988
Nom Area of Cond. | Cond. No. of Wires |  | Nom Thickness of XLPE Insulation |  | Thick- ness of Inner Sheath | Dimen-sion of Armour | Thickness of Outer Sheath |  | Overall Dia of cable (approx) |  | Weight of cable (approx) |  | Max. D.C. Resistance at 200C |  | Max. A.C. Resistance at 900C (Approx) |  | Current Rating |  |  |  | Short Circuit Rating for 1Sec.
|  |  | Arm | Unarm |  | Wire Strip | Arm | Uarm | Arm | Uarm | Armoured | Unarmoured |  |  |  |  | In Ground |  | In Air
mm2 | No |  | mm | mm | mm | mm | mm | mm | mm | mm | Kg/ Km | Kg/ Km | Ohm/km |  | Ohm/km |  | Amps | Amps | Amps | Amps | KA(rms)
| Al | Cu | [8 empty] | Al | Al | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu
4 | 1 | 1 | 1 | 0.7 | NA | 1.4 | 1.24 | 1.8 | 10 | 7.5 | 130 | 70 | 7.41 | 4.61 | 9.45 | 5.89 | 36 | 46 | 31 | 40 | 0.38 | 0.57
6 | 1 | 1 | 1 | 0.7 | NA | 1.4 | 1.24 | 1.8 | 11 | 8.5 | 155 | 85 | 4.61 | 3.08 | 5.89 | 3.93 | 44 | 57 | 39 | 51 | 0.57 | 0.86
10 | 1 | 7 | 1 | 0.7 | NA | 1.4 | 1.24 | 1.8 | 11.5 | 9 | 180 | 105 | 3.08 | 1.83 | 3.93 | 2.34 | 59 | 76 | 53 | 71 | 0.94 | 1.4
16 | 7 | 7 | 1 | 0.7 | NA | 1.4 | 1.24 | 1.8 | 12.5 | 10.5 | 205 | 135 | 1.91 | 1.15 | 2.43 | 1.472 | 76 | 97 | 73 | 95 | 1.5 | 2.3
25 | 7 | 7 | 1.2 | 0.9 | NA | 1.4 | 1.24 | 1.8 | 14.5 | 11.5 | 285 | 170 | 1.2 | 0.727 | 1.535 | 0.93 | 96 | 124 | 98 | 126 | 2.4 | 3.6
35 | 7 | 7 | 1.2 | 0.9 | NA | 1.4 | 1.24 | 1.8 | 15.5 | 12.5 | 330 | 205 | 0.868 | 0.524 | 1.1 | 0.67 | 114 | 148 | 121 | 152 | 3.3 | 5
50 | 7 | 7 | 1.3 | 1 | NA | 1.4 | 1.24 | 1.8 | 17 | 13.5 | 400 | 260 | 0.641 | 0.387 | 0.82 | 0.495 | 135 | 174 | 150 | 189 | 4.7 | 7.1
70 | 19 | 19 | 1.4 | 1.1 | NA | 1.4 | 1.24 | 1.8 | 19.5 | 15.5 | 525 | 340 | 0.443 | 0.268 | 0.567 | 0.343 | 166 | 213 | 187 | 240 | 6.6 | 10
95 | 19 | 19 | 1.4 | 1.1 | NA | 4x0.8 | 1.4 | 1.8 | 20 | 17.5 | 640 | 425 | 0.32 | 0.193 | 0.41 | 0.247 | 198 | 256 | 230 | 297 | 9 | 13.6
120 | 19 | 19 | 1.5 | 1.2 | NA | 4x0.8 | 1.4 | 1.8 | 22 | 19.5 | 750 | 525 | 0.253 | 0.153 | 0.324 | 0.197 | 225 | 289 | 268 | 346 | 11.3 | 17.1
150 | 19 | 19 | 1.7 | 1.4 | NA | 4x0.8 | 1.4 | 2 | 24 | 21.5 | 885 | 645 | 0.206 | 0.124 | 0.264 | 0.161 | 253 | 326 | 309 | 390 | 14.2 | 21.4
185 | 37 | 37 | 1.9 | 1.6 | NA | 4x0.8 | 1.4 | 2 | 26 | 23.5 | 1030 | 780 | 0.164 | 0.0991 | 0.21 | 0.129 | 286 | 366 | 360 | 460 | 17.5 | 26.4
240 | 37 | 37 | 2 | 1.7 | NA | 4x0.8 | 1.4 | 2 | 28.8 | 26.3 | 1280 | 990 | 0.125 | 0.0754 | 0.16 | 0.1 | 332 | 425 | 433 | 552 | 22.6 | 34.3
300 | 37 | 37 | 2.1 | 1.8 | NA | 4x0.8 | 1.56 | 2 | 31.2 | 28.5 | 1530 | 1175 | 0.1 | 0.0601 | 0.13 | 0.081 | 376 | 479 | 501 | 640 | 28.3 | 42.9
400 | 61 | 61 | 2.4 | 2 | NA | 4x0.8 | 1.56 | 2.2 | 34.5 | 32.5 | 1900 | 1525 | 0.0778 | 0.047 | 0.102 | 0.066 | 431 | 544 | 596 | 753 | 37.7 | 57.1
500 | 61 | 61 | 2.6 | 2.2 | NA | 4x0.8 | 1.56 | 2.2 | 38.5 | 36.5 | 2350 | 1890 | 0.0605 | 0.0366 | 0.0809 | 0.053 | 490 | 611 | 693 | 865 | 47.2 | 71.4
630 | 61 | 61 | 2.8 | 2.4 | NA | 4x0.8 | 1.72 | 2.2 | 42.5 | 40.2 | 2850 | 2320 | 0.0469 | 0.0283 | 0.064 | 0.043 | 557 | 684 | 814 | 1001 | 59.4 | 90
800 | 61 | 61 | 3.1 | 2.6 | NA | 4x0.8 | 1.72 | 2.4 | 47.5 | 44 | 3600 | 2940 | 0.0367 | 0.0221 | 0.052 | 0.034 | 632 | 762 | 968 | 1176 | 75.5 | 114.3
1000 | 61 | 61 | 3.3 | 2.8 | NA | 4x0.8 | 1.88 | 2.6 | 52.5 | 48.8 | 4500 | 3660 | 0.0291 | 0.0176 | 0.044 | 0.0281 | 701 | 828 | 1102 | 1299 | 94.3 | 142.9