## 1CoP-I
(Single Core Unarmoured)
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED SINGLE CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
No. of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Nominal Thickness of outer Sheath | Approx Overall Dia of Cable | Approx Nett. Wt. of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[9 empty] | Direct in Ground |  | Direct in Air
[6 empty] | Length | Drum Size |  | For Two Cable | For Three Cable | For Two Cable | For Three Cable
mm2 | No | mm | mm | mm | mm | Kg/Km | Mtrs. | Ohm/Km | Amps. | Amps. | Amps. | Amps.
1 X 1.5 | 1 | 0.8 | 1.8 | 7.2 | 55 | 1000 | 8 | 18.1 | 21 | 17 | 18 | 15
1 X 2.5 | 1 | 0.9 | 1.8 | 7.8 | 67 | 1000 | 8 | 12.1 | 28 | 24 | 25 | 21
1X4 | 1 | 1 | 1.8 | 8.5 | 80 | 1000 | 8 | 7.41 | 36 | 31 | 32 | 27
1X6 | 1 | 1 | 1.8 | 9 | 93 | 1000 | 8 | 4.61 | 44 | 39 | 41 | 35
1X10 | 1 | 1 | 1.8 | 9.8 | 111 | 1000 | 8 | 3.08 | 59 | 51 | 56 | 47
1X16 | 6 | 1 | 1.8 | 11.3 | 155 | 1000 | 8 | 1.91 | 75 | 66 | 72 | 64
1X25 | 6 | 1.2 | 1.8 | 13.1 | 195 | 1000 | 10 | 1.2 | 97 | 86 | 99 | 84
1X35 | 6 | 1.2 | 1.8 | 14.2 | 251 | 1000 | 10 | 0.868 | 120 | 100 | 120 | 105
1X50 | 6 | 1.4 | 1.8 | 15.5 | 295 | 500 | 8 | 0.641 | 145 | 120 | 150 | 130
1X70 | 15 | 1.4 | 1.8 | 17.3 | 387 | 500 | 9 | 0.443 | 170 | 140 | 185 | 155
1X95 | 15 | 1.6 | 1.8 | 19.8 | 510 | 500 | 10 | 0.32 | 205 | 175 | 215 | 190
1X120 | 15 | 1.6 | 2 | 21.5 | 595 | 500 | 10 | 0.253 | 230 | 195 | 240 | 220
1X150 | 15 | 1.8 | 2 | 23.4 | 722 | 500 | 12 | 0.206 | 265 | 220 | 270 | 250
1X185 | 30 | 2 | 2 | 25.7 | 870 | 500 | 12 | 0.164 | 300 | 240 | 305 | 290
1X240 | 30 | 2.2 | 2 | 28.3 | 1099 | 500 | 12 | 0.125 | 335 | 270 | 350 | 335
1X300 | 30 | 2.4 | 2 | 31.9 | 1340 | 500 | 14 | 0.1 | 370 | 295 | 395 | 380
1X400 | 53 | 2.6 | 2.2 | 35.3 | 1660 | 500 | 14 | 0.0778 | 410 | 325 | 455 | 435
1X500 | 53 | 3 | 2.2 | 39 | 2100 | 500 | 16 | 0.0605 | 435 | 345 | 490 | 480
1X630 | 53 | 3.4 | 2.4 | 44 | 2645 | 500 | 16 | 0.0469 | 485 | 390 | 560 | 550
1X800 | 53 | 3.4 | 2.4 | 49 | 3285 | 500 | 16 | 0.0367 | 530 | 440 | 640 | 640
1X1000 | 53 | 3.4 | 2.6 | 53.5 | 3990 | 400 | 16 | 0.0291 | 580 | 490 | 740 | 720
(Two Core Unarmoured)
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED TWIN CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES TYPE AYY
CONFORMING TO IS :- 1554 (Part-1) 1988
No. of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Nominal Thickness of Inner Sheath | Nominal Thickness of Outer Sheath | Approx Overall Dia of Cable | Approx Net. Wt. of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum Size |  | Direct in Ground | Direct in Air
mm2 | No. | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/km | Amps. | Amps.
2 X 1.5 | 1 | 0.8 | 0.3 | 1.8 | 10.5 | 125 | 1000 | 8 | 18.1 | 18 | 16
2 X 2.5 | 1 | 0.9 | 0.3 | 1.8 | 11.85 | 160 | 1000 | 8 | 12.1 | 25 | 21
2X4 | 1 | 1 | 0.3 | 1.8 | 13.5 | 200 | 500 | 8 | 7.41 | 32 | 27
2X6 | 1 | 1 | 0.3 | 1.8 | 14.5 | 240 | 500 | 8 | 4.61 | 40 | 35
2X10 | 1 | 1 | 0.3 | 1.8 | 15.5 | 300 | 500 | 9 | 3.08 | 55 | 47
2X16 | 6 | 1 | 0.3 | 1.8 | 16.6 | 320 | 500 | 9 | 1.91 | 70 | 59
2X25 | 6 | 1.2 | 0.3 | 2 | 18 | 380 | 500 | 9 | 1.2 | 90 | 78
2X35 | 6 | 1.2 | 0.3 | 2 | 20.5 | 460 | 500 | 10 | 0.868 | 110 | 99
2X50 | 6 | 1.4 | 0.3 | 2 | 22.5 | 580 | 500 | 10 | 0.641 | 135 | 125

## 3CoP-IAr
(THREE CORE ARMOURED)
KALINGA - SLS GOLD 1100 VOLTS ARMOURED TYPE 3 CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
Cable Code | No.of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour |  | Min. Thickness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[5 empty] | Round Wire | Steel Strip |  |  |  | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
AYWY | 3x1.5 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 14 | 370 | 500 | 8 | 18.1 | 16 | 13
AYWY | 3x2.5 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 15 | 440 | 500 | 8 | 12.1 | 21 | 18
AYWY | 3x4 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 17 | 530 | 500 | 9 | 7.41 | 28 | 23
AYWY | 3x6 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 18 | 590 | 500 | 10 | 4.61 | 35 | 30
AYWY | 3x10 | 1 | 1 | 0.3 | 1.4 | - | 1.4 | 19.5 | 680 | 500 | 10 | 3.08 | 46 | 40
AYFY | 3x16 | 6 | 1 | 0.3 | - | 4x0.80 | 1.4 | 20 | 690 | 500 | 10 | 1.91 | 60 | 51
AYFY | 3x25 | 6 | 1.2 | 0.3 | - | 4x0.80 | 1.4 | 22.5 | 850 | 500 | 12 | 1.2 | 76 | 70
AYFY | 3x35 | 6 | 1.2 | 0.3 | - | 4x0.80 | 1.4 | 24 | 970 | 500 | 12 | 0.868 | 92 | 86
AYFY | 3x50 | 6 | 1.4 | 0.3 | - | 4x0.80 | 1.56 | 27 | 1200 | 500 | 12 | 0.641 | 110 | 105
AYFY | 3x70 | 15 | 1.4 | 0.4 | - | 4x0.80 | 1.56 | 30.4 | 1510 | 500 | 14 | 0.443 | 135 | 130
AYFY | 3x95 | 15 | 1.6 | 0.4 | - | 4x0.80 | 1.56 | 34 | 1900 | 500 | 14 | 0.32 | 165 | 155
AYFY | 3x120 | 15 | 1.6 | 0.4 | - | 4x0.80 | 1.72 | 37 | 2200 | 500 | 14 | 0.253 | 185 | 180
AYFY | 3x150 | 15 | 1.8 | 0.5 | - | 4x0.80 | 1.88 | 41.5 | 2600 | 500 | 16 | 0.206 | 210 | 205
AYFY | 3x185 | 30 | 2 | 0.5 | - | 4x0.80 | 1.88 | 45 | 3100 | 500 | 16 | 0.164 | 235 | 240
AYFY | 3x240 | 30 | 2.2 | 0.6 | - | 4x0.80 | 2.2 | 51 | 3900 | 500 | 18 | 0.125 | 275 | 280
AYFY | 3x300 | 30 | 2.4 | 0.6 | - | 4x0.80 | 2.36 | 56 | 4650 | 350 | 18 | 0.1 | 305 | 315
AYFY | 3x400 | 53 | 2.6 | 0.7 | - | 4x0.80 | 2.52 | 62.5 | 5900 | 350 | 20 | 0.0778 | 335 | 375
AYFY | 3x500 | 53 | 3 | 0.7 | - | 4x0.80 | 2.84 | 69.5 | 7100 | 250 | 20 | 0.0605 | 365 | 420
(Three & Half CORE ARMOURED)
KALINGA - SLS GOLD 1100 VOLTS ARMOURED 3.5 CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
Cable Code | No.of Cores & Cross Sectional Area | Min. No. of Wires in Conduct-or | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour Steel Strip | Min. Thickness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[9 empty] | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
AYFY | 3.5x25/16 | 6/6 | 1.2/1.0 | 0.3 | 4x0.80 | 1.4 | 23.8 | 985 | 500 | 12 | 1.20/1.91 | 76 | 70
AYFY | 3.5x35/16 | 6/6 | 1.2/1.0 | 0.3 | 4x0.80 | 1.4 | 25.5 | 1090 | 500 | 12 | 0.868/1.91 | 92 | 86
AYFY | 3.5x50/25 | 6/6 | 1.4/1.2 | 0.3 | 4x0.80 | 1.56 | 29 | 1380 | 500 | 14 | 0.641/1.20 | 110 | 105
AYFY | 3.5x70/35 | 15/6 | 1.4/1.2 | 0.4 | 4x0.80 | 1.56 | 33 | 1670 | 500 | 14 | 0.443/0.868 | 135 | 130
AYFY | 3.5x95/50 | 15/6 | 1.6/1.4 | 0.4 | 4x0.80 | 1.56 | 37 | 2125 | 500 | 14 | 0.320/0.641 | 165 | 155
AYFY | 3.5x120/70 | 15/15 | 1.6/1.4 | 0.5 | 4x0.80 | 1.72 | 41 | 2510 | 500 | 16 | 0.253/0.443 | 185 | 180
AYFY | 3.5x150/70 | 15/16 | 1.8/1.4 | 0.5 | 4x0.80 | 1.88 | 45 | 2930 | 500 | 16 | 0.206/0.443 | 210 | 205
AYFY | 3.5x185/95 | 30/15 | 2.0/1.6 | 0.5 | 4x0.80 | 2.04 | 49.5 | 3540 | 500 | 18 | 0.164/0.320 | 235 | 240
AYFY | 3.5x240/120 | 30/15 | 2.2/1.6 | 0.6 | 4x0.80 | 2.2 | 55 | 4800 | 500 | 20 | 0.125/0.253 | 275 | 280
AYFY | 3.5x300/150 | 30/15 | 2.4/1.8 | 0.6 | 4x0.80 | 2.36 | 61 | 5700 | 350 | 18 | 0.100/0.206 | 305 | 315
AYFY | 3.5x400/185 | 53/30 | 2.6/2.0 | 0.7 | 4x0.80 | 2.68 | 68.5 | 6700 | 300 | 20 | 0.0778/0.164 | 335 | 375
AYFY | 3.5x500/240 | 53/30 | 3.0/2.0 | 0.7 | 4x0.80 | 2.84 | 76 | 8000 | 200 | 20 | 0.0605/0.125 | 365 | 420

## 3CoP-IUr
(Three Core Unarmoured)
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED 3 CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
No. of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Nominal Thickness of Inner Sheath | Nominal Thickness of PVC Outer Sheath | Approx Overall Dia of Cable | Approx Nett. Wt. of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum Size |  | Direct in Ground | Direct in Air
mm2 | No | mm | mm | mm | mm | mm | Kg/Km | Mtrs. | Ohm/Km | Amps. | Amps.
3 X 1.5 | 1 | 0.8 | 0.3 |  | 10.6 | 125 | 1000 | 8 | 18.1 | 16 | 13
3 X 2.5 | 1 | 0.9 | 0.3 | 1.8 | 11.9 | 155 | 500 | 8 | 12.1 | 21 | 18
3X4 | 1 | 1 | 0.3 | 1.8 | 13.4 | 220 | 500 | 8 | 7.41 | 28 | 23
3X6 | 1 | 1 | 0.3 | 1.8 | 14.5 | 265 | 500 | 8 | 4.61 | 35 | 30
3X10 | 1 | 1 | 0.3 | 1.8 | 16.2 | 360 | 500 | 9 | 3.08 | 46 | 40
3X16 | 6 | 1 | 0.3 | 1.8 | 17.5 | 400 | 500 | 10 | 1.91 | 60 | 51
3X25 | 6 | 1.2 | 0.3 | 2 | 21 | 510 | 500 | 10 | 1.2 | 76 | 70
3X35 | 6 | 1.2 | 0.3 | 2 | 22.4 | 610 | 500 | 12 | 0.868 | 92 | 86
3X50 | 6 | 1.4 | 0.3 | 2 | 24.9 | 795 | 500 | 12 | 0.641 | 110 | 105
3X70 | 15 | 1.4 | 0.4 | 2.2 | 27.7 | 1020 | 500 | 12 | 0.443 | 135 | 130
3X95 | 15 | 1.6 | 0.4 | 2.2 | 31.6 | 1355 | 500 | 14 | 0.32 | 165 | 155
3X120 | 15 | 1.6 | 0.4 | 2.2 | 33.7 | 1625 | 500 | 14 | 0.253 | 185 | 180
3X150 | 15 | 1.8 | 0.5 | 2.4 | 37.9 | 1955 | 500 | 16 | 0.206 | 210 | 205
3X185 | 30 | 2 | 0.5 | 2.6 | 41 | 2390 | 500 | 16 | 0.164 | 235 | 240
3X240 | 30 | 2.2 | 0.6 | 2.8 | 46.7 | 3100 | 500 | 18 | 0.125 | 275 | 280
3X300 | 30 | 2.4 | 0.6 | 3 | 49.9 | 3800 | 350 | 18 | 0.1 | 305 | 315
3X400 | 53 | 2.6 | 0.6 | 3.4 | 57.9 | 4900 | 350 | 20 | 0.0778 | 335 | 375
3X500 | 53 | 3 | 0.7 | 3.6 | 65.2 | 6000 | 300 | 20 | 0.0605 | 365 | 420
(Three & Half Core Unarmoured)
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED 3.5 CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
No. of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Nominal Thickness of Inner Sheath | Nominal Thickness of PVC Outer Sheath | Approx Overall Dia of Cable | Approx Nett. Wt. of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum Size |  | Direct in Ground | Direct in Air
mm2 | No | mm | mm | mm | mm | mm | Kg/Km | Mtrs. | Ohm/Km | Amps. | Amps.
3.5x25/16 | 6/6 | 1.2/1.0 | 0.3 | 2 | 23 | 615 | 500 | 12 | 1.20/1.91 | 76 | 70
3.5x35/16 | 6/6 | 1.2/1.1 | 0.3 | 2 | 25 | 720 | 500 | 12 | 0.868/1.91 | 92 | 86
3.5x50/25 | 6/6 | 1.4/1.2 | 0.3 | 2 | 28.5 | 950 | 500 | 12 | 0.641/1.20 | 110 | 105
3.5x70/35 | 15/6 | 1.4/1.3 | 0.4 | 2.2 | 31.5 | 1200 | 500 | 14 | 0.443/0.868 | 135 | 130
3.5x95/50 | 15/6 | 1.6/1.4 | 0.4 | 2.2 | 35 | 1610 | 500 | 14 | 0.320/0.641 | 165 | 155
3.5x120/70 | 15/15 | 1.6/1.4 | 0.5 | 2.4 | 39.5 | 1950 | 500 | 16 | 0.253/0.443 | 185 | 180
3.5x150/70 | 15/15 | 1.8/1.4 | 0.5 | 2.4 | 43.5 | 2300 | 500 | 16 | 0.206/0.443 | 210 | 205
3.5x185/95 | 30/15 | 2.0/1.6 | 0.5 | 2.6 | 48 | 2875 | 500 | 18 | 0.164/0.320 | 235 | 240
3.5x240/120 | 30/15 | 2.2/1.6 | 0.6 | 3 | 54 | 3650 | 500 | 20 | 0.125/0.253 | 275 | 280
3.5x300/150 | 30/15 | 2.4/1.8 | 0.6 | 3.2 | 60 | 4500 | 350 | 18 | 0.100/0.206 | 305 | 315
3.5x400/185 | 53/30 | 2.6/2.0 | 0.7 | 3.4 | 66.5 | 5700 | 350 | 20 | 0.0778/0.164 | 335 | 375
3.5x500/240 | 53/30 | 3.0/2.2 | 0.7 | 3.8 | 75.5 | 7200 | 250 | 20 | 0.0605/0.125 | 365 | 420

## 4CoP-IUr
(Four Core Unarmoured)
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED 4CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
No.of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Nominal Thickness of PVC outer sheath | Approx overall Dia of Cable | Approx Net. Wt. of Cable | Standard Delivery |  | Max. D.C Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum |  | Direct in Ground |  | Direct in Air
mm2 | No | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. |  | Amps.
4x1.5 | 1 | 0.8 | 0.3 | 1.8 | 11.5 | 150 | 1000 | 8 | 18.1 | 16 |  | 13
4x2.5 | 1 | 0.9 | 0.3 | 1.8 | 13.5 | 190 | 500 | 8 | 12.1 | 21 |  | 18
4x4 | 1 | 1 | 0.3 | 1.8 | 15 | 240 | 500 | 8 | 7.41 | 28 |  | 23
4x6 | 1 | 1 | 0.3 | 1.8 | 16.5 | 300 | 500 | 9 | 4.61 | 35 |  | 30
4x10 | 1 | 1 | 0.3 | 1.8 | 18.5 | 400 | 500 | 10 | 3.08 | 46 |  | 40
4x16 | 6 | 1 | 0.3 | 2 | 20 | 505 | 500 | 10 | 1.91 | 60 |  | 51
4x25 | 6 | 1.2 | 0.3 | 2 | 23.5 | 650 | 500 | 12 | 1.2 | 76 |  | 70
4x35 | 6 | 1.2 | 0.3 | 2 | 26.5 | 850 | 500 | 12 | 0.868 | 92 |  | 86
4x50 | 6 | 1.4 | 0.4 | 2.2 | 29.5 | 1100 | 500 | 12 | 0.641 | 110 |  | 105
4x70 | 15 | 1.4 | 0.4 | 2.2 | 32.5 | 1380 | 500 | 14 | 0.443 | 135 |  | 130
4x95 | 15 | 1.6 | 0.4 | 2.4 | 37 | 1800 | 500 | 16 | 0.32 | 165 |  | 155
4x120 | 15 | 1.6 | 0.5 | 2.4 | 41 | 2100 | 500 | 16 | 0.253 | 185 |  | 180
4x150 | 15 | 1.8 | 0.5 | 2.6 | 45 | 2650 | 500 | 16 | 0.206 | 210 |  | 205
4x185 | 30 | 2 | 0.6 | 2.8 | 50.5 | 3250 | 500 | 18 | 0.164 | 235 |  | 240
4x240 | 30 | 2.2 | 0.6 | 3 | 56 | 4100 | 500 | 20 | 0.125 | 275 |  | 280
4x300 | 30 | 2.4 | 0.7 | 3.4 | 61.8 | 5020 | 350 | 20 | 0.1 | 305 |  | 315
PVC ARMOURED CABLE (Twin Core Armoured)
KALINGA - SLS GOLD 1100 VOLTS ARMOURED TYPE TWIN CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
Cable Code | No.of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour |  | Min. Thick ness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  |  | Current Rating
[5 empty] | Round Wire | Steel Strip |  |  |  | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
AYWY | 2x1.5 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 13.5 | 330 | 500 | 8 | 18.1 | 18 | 16
AYWY | 2x2.5 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 14.5 | 400 | 500 | 8 | 12.1 | 25 | 21
AYWY | 2x4.0 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 16 | 465 | 500 | 8 | 7.41 | 32 | 27
AYWY | 2x6.0 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 17 | 520 | 500 | 9 | 4.61 | 40 | 35
AYWY | 2x10 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 18 | 600 | 500 | 10 | 3.08 | 55 | 47
AYFY | 2x16 | 6 | 1 | 0.3 | - | 4x0.8 | 1.4 | 18.5 | 580 | 500 | 10 | 1.91 | 70 | 59
AYFY | 2x25 | 6 | 1.2 | 0.3 | - | 4x0.8 | 1.4 | 20 | 650 | 500 | 10 | 1.2 | 90 | 78
AYFY | 2x35 | 6 | 1.2 | 0.3 | - | 4x0.8 | 1.4 | 22 | 755 | 500 | 10 | 0.868 | 110 | 99
AYFY | 2x50 | 6 | 1.4 | 0.3 | - | 4x0.8 | 1.4 | 24 | 920 | 500 | 12 | 0.641 | 135 | 125
AYFY | 2x70 | 15 | 1.4 | 0.4 | - | 4x0.8 | 1.56 | 28 | 1080 | 500 | 12 | 0.443 | 160 | 150

## 4CoP-IAr
(Four Core Armoured)
KALINGA - SLS GOLD 1100 VOLTS ARMOURED TYPE 4CORE PVC INSULATED
ALUMINIUM CONDUCTOR POWER CABLES
CONFORMING TO IS :- 1554 (Part-1) 1988
Cable Code | No.of Cores & Cross Sectional Area | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour |  | Min. Thickness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[5 empty] | Round Wire | Steel Strip |  |  |  | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
AYWY | 4x1.5 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 14.5 | 400 | 500 | 8 | 18.1 | 16 | 13
AYWY | 4x2.5 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 16 | 475 | 500 | 9 | 12.1 | 21 | 18
AYWY | 4x4.0 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 17.6 | 576 | 500 | 10 | 7.41 | 28 | 23
AYWY | 4x6.0 | 1 | 1 | 0.3 | 1.4 | - | 1.24 | 19.5 | 660 | 500 | 10 | 4.61 | 35 | 30
AYFY | 4x10 | 1 | 1 | 0.3 | - | 4x0.80 | 1.4 | 20.5 | 710 | 500 | 10 | 3.08 | 40 | 40
AYFY | 4x16 | 6 | 1 | 0.3 | - | 4x0.80 | 1.4 | 22 | 810 | 500 | 12 | 1.91 | 60 | 51
AYFY | 4x25 | 6 | 1.2 | 0.3 | - | 4x0.80 | 1.4 | 25 | 1020 | 500 | 12 | 1.2 | 76 | 70
AYFY | 4x35 | 6 | 1.2 | 0.3 | - | 4x0.80 | 1.4 | 28 | 1250 | 500 | 14 | 0.868 | 92 | 86
AYFY | 4x50 | 6 | 1.4 | 0.4 | - | 4x0.80 | 1.56 | 31.5 | 1540 | 500 | 14 | 0.641 | 110 | 105
AYFY | 4x70 | 15 | 1.4 | 0.4 | - | 4x0.80 | 1.56 | 34 | 1840 | 500 | 14 | 0.443 | 135 | 130
AYFY | 4x95 | 15 | 1.6 | 0.4 | - | 4x0.80 | 1.72 | 38 | 2362 | 500 | 16 | 0.32 | 165 | 155
AYFY | 4x120 | 15 | 1.6 | 0.5 | - | 4x0.80 | 1.88 | 42 | 2700 | 500 | 16 | 0.253 | 185 | 180
AYFY | 4x150 | 15 | 1.8 | 0.5 | - | 4x0.80 | 1.88 | 46 | 3250 | 500 | 16 | 0.206 | 210 | 205
AYFY | 4x185 | 30 | 2 | 0.6 | - | 4x0.80 | 2.04 | 50.8 | 3900 | 500 | 18 | 0.164 | 235 | 240
AYFY | 4x240 | 30 | 2.2 | 0.6 | - | 4x0.80 | 2.36 | 56.8 | 5100 | 500 | 20 | 0.125 | 275 | 280
AYFY | 4x300 | 30 | 2.4 | 0.7 | - | 4x0.80 | 2.52 | 64.5 | 6100 | 300 | 20 | 0.1 | 305 | 315

## 2.5mmP-II
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED TYPE PVC INSULATED
COPPER CONDUCTOR CONTROL CABLES TYPE YY
CONFORMING TO IS :- 1554 (Part-1) 1988
Nominal Area of Conductor 2.5mm2
No.of Cores | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Nominal Thickness of PVC outer sheath | Approx overall Dia of Cable | Approx Net. Wt. of Cable | Standard Delivery |  | Max. Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum |  | Direct in Ground | Direct in Air
| No | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
2 | 1 | 0.9 | 0.3 | 1.8 | 12 | 195 | 1000 | 8 | 7.41 | 32 | 27
3 | 1 | 0.9 | 0.3 | 1.8 | 13 | 235 | 1000 | 8 | 7.41 | 27 | 24
4 | 1 | 0.9 | 0.3 | 1.8 | 14 | 290 | 500 | 8 | 7.41 | 27 | 24
5 | 1 | 0.9 | 0.3 | 1.8 | 15 | 325 | 500 | 8 | 7.41 | 23 | 19
6 | 1 | 0.9 | 0.3 | 1.8 | 16 | 360 | 500 | 8 | 7.41 | 22 | 18
7 | 1 | 0.9 | 0.3 | 1.8 | 16 | 400 | 500 | 8 | 7.41 | 20 | 17
8 | 1 | 0.9 | 0.3 | 1.8 | 16.5 | 435 | 500 | 8 | 7.41 | 19 | 16
9 | 1 | 0.9 | 0.3 | 1.8 | 17.5 | 480 | 500 | 9 | 7.41 | 19 | 16
10 | 1 | 0.9 | 0.3 | 1.8 | 19 | 530 | 500 | 9 | 7.41 | 18 | 15
12 | 1 | 0.9 | 0.3 | 2 | 20 | 590 | 500 | 10 | 7.41 | 17 | 14
14 | 1 | 0.9 | 0.3 | 2 | 20.5 | 680 | 500 | 10 | 7.41 | 16 | 13
16 | 1 | 0.9 | 0.3 | 2 | 21.5 | 760 | 500 | 10 | 7.41 | 15 | 13
19 | 1 | 0.9 | 0.3 | 2 | 23 | 890 | 500 | 10 | 7.41 | 14 | 12
24 | 1 | 0.9 | 0.3 | 2 | 26.5 | 1050 | 500 | 12 | 7.41 | 13 | 11
27 | 1 | 0.9 | 0.3 | 2 | 27 | 1150 | 500 | 12 | 7.41 | 12 | 10
30 | 1 | 0.9 | 0.3 | 2 | 28.5 | 1250 | 500 | 12 | 7.41 | 12 | 10
37 | 1 | 0.9 | 0.4 | 2.2 | 31 | 1580 | 500 | 14 | 7.41 | 11 | 9
44 | 1 | 0.9 | 0.4 | 2.2 | 34 | 1820 | 500 | 14 | 7.41 | 10 | 9
52 | 1 | 0.9 | 0.4 | 2.2 | 36 | 2100 | 500 | 14 | 7.41 | 10 | 8
61 | 1 | 0.9 | 0.4 | 2.2 | 38 | 2400 | 500 | 16 | 7.41 | 9 | 8

## 4CoP-II
KALINGA - SLS GOLD 1100 VOLTS ARMOURED 4 CORE PVC INSULATED
COPPER CONDUCTOR CONTROL CABLES TYPE-YWY/YFY
CONFORMING TO IS :- 1554 (Part-1) 1988
Nominal Area of Conductor 2.5mm2
Cable Code | No.of Cores | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour |  | Min. Thickness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[5 empty] | Round Wire | Steel Strip |  |  |  | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
YWY | 2 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 15 | 480 | 500/1000 | 8 | 7.41 | 32 | 27
YWY | 3 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 15.5 | 530 | 500/1000 | 8 | 7.41 | 27 | 24
YWY | 4 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 16 | 590 | 500/1000 | 9 | 7.41 | 27 | 24
YWY | 5 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 17 | 680 | 500/1000 | 9 | 7.41 | 23 | 19
YWY | 6 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 18 | 730 | 500/1000 | 9 | 7.41 | 22 | 18
YWY | 7 | 1 | 0.9 | 0.3 | 1.4 | - | 1.24 | 18 | 755 | 500/1000 | 9 | 7.41 | 20 | 17
YWY | 8 | 1 | 0.9 | 0.3 | 1.4 | - | 1.4 | 18.3 | 780 | 500/1000 | 10 | 7.41 | 19 | 16
YFY | 9 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 19.4 | 810 | 500/1000 | 10 | 7.41 | 19 | 16
YFY | 10 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 20.6 | 850 | 500/1000 | 10 | 7.41 | 18 | 15
YFY | 12 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 21.5 | 950 | 500 | 10 | 7.41 | 17 | 14
YFY | 14 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 22 | 1030 | 500 | 10 | 7.41 | 16 | 13
YFY | 16 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 23 | 1130 | 500 | 12 | 7.41 | 15 | 13
YFY | 19 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 24.5 | 1260 | 500 | 12 | 7.41 | 14 | 12
YFY | 24 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 27.7 | 1510 | 500 | 12 | 7.41 | 13 | 11
YFY | 27 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.4 | 28.3 | 1600 | 500 | 12 | 7.41 | 12 | 10
YFY | 30 | 1 | 0.9 | 0.3 | - | 4X0.80 | 1.56 | 29.6 | 1750 | 500 | 14 | 7.41 | 12 | 10
YFY | 37 | 1 | 0.9 | 0.4 | - | 4X0.80 | 1.56 | 31.9 | 2020 | 500 | 14 | 7.41 | 11 | 9
YFY | 44 | 1 | 0.9 | 0.4 | - | 4X0.80 | 1.56 | 35.5 | 2365 | 500 | 14 | 7.41 | 10 | 9
YFY | 52 | 1 | 0.9 | 0.4 | - | 4X0.80 | 1.56 | 37 | 2700 | 500 | 16 | 7.41 | 10 | 8
YFY | 61 | 1 | 0.9 | 0.4 | - | 4X0.80 | 1.56 | 39.1 | 3000 | 500 | 16 | 7.41 | 9 | 8

## Sheet4PartII
KALINGA - SLS GOLD 1100 VOLTS ARMOURED TYPE PVC INSULATED
COPPER CONDUCTOR CONTROL CABLES TYPE-YWY/YFY
CONFORMING TO IS :- 1554 (Part-1) 1988
Nominal Area of Conductor 1.5mm2
Cable Code | No.of Cores | Min. No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Armour |  | Min. Thickness of PVC outer sheath | Approx Overall Dia of Cable | Approx Net.W.t of Cables | Standard Delivery |  | Max. D.C. Conductor Resistance at 200C | Current Rating
[5 empty] | Round Wire | Steel Strip |  |  |  | Length | Drum Size |  | Direct in Ground | Direct in Air
| mm2 | No. | mm | mm | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
YWY | 2 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 13.5 | 410 | 500/1000 | 8 | 12.1 | 23 | 20
YWY | 3 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 14 | 460 | 500/1000 | 8 | 12.1 | 21 | 17
YWY | 4 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 15 | 515 | 500/1000 | 8 | 12.1 | 21 | 17
YWY | 5 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 15.5 | 550 | 500/1000 | 9 | 12.1 | 17 | 14
YWY | 6 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 17 | 610 | 500/1000 | 9 | 12.1 | 15 | 13
YWY | 7 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 17 | 620 | 500/1000 | 9 | 12.1 | 14 | 13
YWY | 8 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 17 | 630 | 500/1000 | 9 | 12.1 | 14 | 12
YWY | 9 | 1 | 0.8 | 0.3 | 1.4 | - | 1.24 | 18 | 690 | 500/1000 | 9 | 12.1 | 13 | 12
YWY | 10 | 1 | 0.8 | 0.3 | 1.4 | - | 1.4 | 20 | 820 | 500/1000 | 10 | 12.1 | 13 | 11
YFY | 12 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.24 | 20.5 | 750 | 500 | 10 | 12.1 | 12 | 10
YFY | 14 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 21 | 820 | 500 | 10 | 12.1 | 11 | 10
YFY | 16 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 21.5 | 900 | 500 | 10 | 12.1 | 11 | 9
YFY | 19 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 22 | 985 | 500 | 12 | 12.1 | 10 | 9
YFY | 24 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 25 | 1170 | 500 | 12 | 12.1 | 9 | 8
YFY | 27 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 26 | 1250 | 500 | 12 | 12.1 | 9 | 8
YFY | 30 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 27 | 1355 | 500 | 12 | 12.1 | 9 | 7
YFY | 37 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.4 | 29 | 1580 | 500 | 14 | 12.1 | 8 | 7
YFY | 44 | 1 | 0.8 | 0.3 | - | 4X0.80 | 1.56 | 31 | 1780 | 500 | 14 | 12.1 | 7 | 6
YFY | 52 | 1 | 0.8 | 0.4 | - | 4X0.80 | 1.56 | 33 | 2040 | 500 | 14 | 12.1 | 7 | 6
YFY | 61 | 1 | 0.8 | 0.4 | - | 4X0.80 | 1.56 | 35 | 2240 | 500 | 14 | 12.1 | 6 | 6

## Sheet3PartII
KALINGA - SLS GOLD 1100 VOLTS UN-ARMOURED PVC INSULATED
COPPER CONDUCTOR CONTROL CABLES TYPE YY
CONFORMING TO IS :- 1554 (Part-1) 1988
Nominal Area of Conductor 1.5mm2
No.of Cores | No. of Wires in Conductor | Nominal Thickness of PVC Insulation | Min. Thickness of Inner Sheath | Nominal Thickness of PVC outer sheath | Approx overall Dia of Cable | Approx Net. Wt. of Cable | Standard Delivery |  | Max. D.C Conductor Resistance at 200C | Current Rating
[7 empty] | Length | Drum |  | Direct in Ground | Direct in Air
| No | mm | mm | mm | mm | Kg/Km | Mtrs. |  | Ohm/Km | Amps. | Amps.
2 | 1 | 0.8 | 0.3 | 1.8 | 11.5 | 165 | 1000 | 8 | 12.1 | 23 | 20
3 | 1 | 0.8 | 0.3 | 1.8 | 11.8 | 190 | 1000 | 8 | 12.1 | 21 | 17
4 | 1 | 0.8 | 0.3 | 1.8 | 12.6 | 225 | 1000 | 8 | 12.1 | 21 | 17
5 | 1 | 0.8 | 0.3 | 1.8 | 13.2 | 260 | 500 | 8 | 12.1 | 17 | 14
6 | 1 | 0.8 | 0.3 | 1.8 | 14.2 | 290 | 500 | 8 | 12.1 | 15 | 13
7 | 1 | 0.8 | 0.3 | 1.8 | 14.2 | 310 | 500 | 8 | 12.1 | 14 | 13
8 | 1 | 0.8 | 0.3 | 1.8 | 14.5 | 340 | 500 | 8 | 12.1 | 14 | 12
9 | 1 | 0.8 | 0.3 | 1.8 | 15 | 360 | 500 | 8 | 12.1 | 13 | 12
10 | 1 | 0.8 | 0.3 | 1.8 | 17.5 | 415 | 500 | 9 | 12.1 | 13 | 11
12 | 1 | 0.8 | 0.3 | 1.8 | 18 | 450 | 500 | 9 | 12.1 | 12 | 10
14 | 1 | 0.8 | 0.3 | 1.8 | 19 | 490 | 500 | 9 | 12.1 | 11 | 10
16 | 1 | 0.8 | 0.3 | 1.8 | 20 | 560 | 500 | 9 | 12.1 | 11 | 9
19 | 1 | 0.8 | 0.3 | 2 | 21 | 640 | 500 | 10 | 12.1 | 10 | 9
24 | 1 | 0.8 | 0.3 | 2 | 23.5 | 790 | 500 | 10 | 12.1 | 9 | 8
27 | 1 | 0.8 | 0.3 | 2 | 24.5 | 825 | 500 | 12 | 12.1 | 9 | 8
30 | 1 | 0.8 | 0.3 | 2 | 25.5 | 900 | 500 | 12 | 12.1 | 9 | 7
37 | 1 | 0.8 | 0.3 | 2 | 27 | 1060 | 500 | 12 | 12.1 | 8 | 7
44 | 1 | 0.8 | 0.3 | 2 | 30 | 1210 | 500 | 12 | 12.1 | 7 | 6
52 | 1 | 0.8 | 0.4 | 2.2 | 31.5 | 1430 | 500 | 14 | 12.1 | 7 | 6
61 | 1 | 0.8 | 0.4 | 2.2 | 34 | 1665 | 500 | 14 | 12.1 | 6 | 6